## ACCS-HEB
Parameter sheet of Air-cooled split system-Horizontal evaporator blower
DB Model | Outdoor unit |  | ACCS12(HP) | ACCS20(HP) | ACCS25(HP) | ACCS32(HP) | ACCS36(HP) | ACCS42(HP) | DB Model | Outdoor unit |  | ACCS48(HP) | ACCS52(HP) | ACCS62(HP) | ACCS72(HP) | ACCS83(HP) | ACCS104(HP)
| Indoor unit |  | HEB12(HP) | HEB20(HP) | HEB25(HP) | HEB32(HP) | HEB36(HP) | HEB42(HP) |  | Indoor unit |  | HEB48(HP) | HEB52(HP) | HEB62(HP) | HEB72(HP) | HEB88(HP) | HEB104(HP)
Nominal cooling capacity |  | kW | 12.5 | 19.5 | 24.8 | 31.2 | 35.6 | 41.3 | Nominal cooling capacity |  | kW | 47.4 | 51.3 | 63.3 | 71.3 | 87.9 | 103.7
|  | Kcal/h | 10750 | 16747 | 21364 | 26796 | 30598 | 35498 |  |  | Kcal/h | 40737 | 44086 | 54406 | 61286 | 75570 | 89144
Nominal Heating capacity |  | kW | 14.6 | 22.6 | 28.9 | 35.8 | 40.8 | 46.9 | Nominal Heating capacity |  | kW | 54.4 | 58.9 | 72.6 | 81.9 | 100 | 115.8
|  | Kcal/h | 12542 | 19463 | 24895 | 30779 | 35124 | 40375 |  |  | Kcal/h | 46802 | 50695 | 62463 | 70429 | 86000 | 99579
Power supply | Outdoor unit |  | 380V/3PH/50HZ | [5 empty] | Power supply | Outdoor unit |  | 380V/3PH/50HZ
| Indoor unit |  | 220V/1PH/50Hz |  |  |  |  | 380V/3PH/50Hz |  | Indoor unit |  | 380V/3PH/50HZ
Inrush current |  | A | 65.8 | 2x46.2 | 2x65.8 | 2x65.8 | 155 | 105+65.8 | Inrush current |  | A | 127+65.8 | 155+65.8 | 2x127 | 2x155 | 2x135 | 2x175
Rated input power | Cooling | kW | 4.63 | 7.2 | 9.3 | 11.8 | 12.8 | 15.1 | Rated input power | Cooling | kW | 17.9 | 18.4 | 23.1 | 26.6 | 28.1 | 39.3
| Heating | kW | 4.5 | 7.13 | 9.21 | 11.68 | 12.67 | 14.95 |  | Heating | kW | 17.72 | 18.22 | 22.87 | 26.33 | 27.82 | 38.91
Rated input current | Cooling | A | 8.24 | 12.87 | 16.62 | 21.09 | 22.88 | 26.99 | Rated input current | Cooling | A | 32 | 32.89 | 41.29 | 47.55 | 50.23 | 70.25
| Heating | A | 8.02 | 12.74 | 16.46 | 20.88 | 22.65 | 26.72 |  | Heating | A | 31.68 | 32.56 | 40.88 | 47.08 | 49.7 | 69.55
Outline dimensions L*W*H | Outdoor unit | mm | 950x340×1250 | 1120×830x1030 | 1120×830x1030 | 1180x960x1130 | 1180x960x1130 | 1640×880×1130 | Outline dimensions L*W*H | Outdoor unit | mm | 1640x880x1130 | 1840x970x1130 | 1840x970x1130 | 2120×970x1130 | 2243×1250x1380 | 2243x1250x1580
| Indoor unit | mm | 1460x335x390 | 1660x915×480 | 1660×915×480 | 1660×915x580 | 1790×915x580 | 1840x1045×680 |  | Indoor unit | mm | 2065x1160x680 | 2165x1160x680 | 1870x1230x980 | 1870x1230x1080 | 2100×1270x1180 | 2100x1270×1280
Noise | Outdoor unit | dB(A) | ≤62 | ≤67 | ≤67 | ≤68 | ≤70 | ≤71 | Noise | Outdoor unit | dB(A) | ≤71 | ≤71 | ≤71 | ≤71 | ≤71 | ≤71
| Indoor unit | dB(A) | ≤60 | ≤64 | ≤64 | ≤66 | ≤66 | ≤68 |  | Indoor unit | dB(A) | ≤68 | ≤68 | ≤68 | ≤69 | ≤69 | ≤70
Indoor unit blower | Air flowrate | m3/h | 2000 | 3500 | 4500 | 5650 | 6450 | 7400 | Indoor unit blower | Air flowrate | m3/h | 8550 | 9250 | 11450 | 12900 | 14800 | 17100
| ERP | Pa | 30 | 120 | 100 | 150 | 130 | 180 |  | ERP | Pa | 200 | 200 | 300 | 300 | 280 | 500
Indoor/Outdoor connection type |  |  | Welding/Threaded connection | [5 empty] | Indoor/Outdoor connection type |  |  | Welding/Threaded connection
Piping dimension | Liquid φ | mm | 12.7 | 9.52×2 | 12.7x2 | 12.7×2 | 15.88 | 15.88/12.7 | Piping dimension | Liquid φ | mm | 15.88/12.7 | 15.88/12.7 | 15.88X2 | 15.88X2 | 15.88X2 | 19.05X2
| Gas φ | mm | 19.05 | 15.88×2 | 19.05×2 | 19.05x2 | 28 | 28/19.05 |  | Gas φ | mm | 28/19.05 | 28/19.05 | 28X2 | 28X2 | 28X2 | 35X2
Condensing water pipe dimension |  | mm | DN25 | DN25 | DN25 | DN25 | DN25 | DN25 | Condensing water pipe dimension |  | mm | DN25 | DN25 | DN25 | DN25 | DN25 | DN25
Refrigerant gas R410a/R407c | Charge amount | kg | 4.2 | 3.0×2 | 4x2 | 4.5×2 | 10.5 | 9+4.5 | Refrigerant gas R410a/R407c | Charge amount | kg | 9.5+4.5 | 10+4.5 | 9.5X2 | 10.5X2 | 12X2 | 15X2
Shipping weight | Outdoor unit | kg | 75 | 170 | 180 | 220 | 230 | 260 | Shipping weight | Outdoor unit | kg | 280 | 230 | 340 | 460 | 600 | 650
| Indoor unit | kg | B0 | 90 | 100 | 150 | 160 | 180 |  | Indoor unit | kg | 200 | 220 | 230 | 300 | 320 | 400
Electrical heater(Option) |  | kW | 1×4 | 2x3 | 2x4 | 2×5 | 2x6 | 2x6 | Electrical heater(Option) |  | kW | 2X8 | 2X8 | 2X10 | 2X10 | 2X12 | 2X14
Hot water coil (Option) | Heating capacity | kW | 14.3 | 22.2 | 28.4 | 35.1 | 40 | 46 | Hot water coil (Option) | Heating capacity | kW | 53.3 | 57.8 | 71.2 | 80.3 | 98 | 113.5
| Water flowrate | m3/h | 1.23 | 1.91 | 2.44 | 3.02 | 3.44 | 3.96 |  | Water flowrate | m3/h | 4.59 | 4.97 | 6.12 | 6.9 | 8.43 | 9.76
Notes：1.The cooling capacity is measured under the conditions of nominal air volume, with indoor DB/WB 27/19℃ and outdoor DB/WB 35/24℃; | [8 empty] | Notes：1.The cooling capacity is measured under the conditions of nominal air volume, with indoor DB/WB 27/19℃ and outdoor DB/WB 35/24℃;
2.The heating capacity is measured under the conditions of nominal air volume, with indoor DB/WB 20/15℃ and outdoor DB/WB 7/6℃; | [8 empty] | 2.The heating capacity is measured under the conditions of nominal air volume, with indoor DB/WB 20/15℃ and outdoor DB/WB 7/6℃;
3.The hot water coil capacity is measured under the conditions of nominal air volume, with hot water inlet/outlet 60/50℃ and air inlet 30℃; | [8 empty] | 3.The hot water coil capacity is measured under the conditions of nominal air volume, with hot water inlet/outlet 60/50℃ and air inlet 30℃;
4.The above parameters are subject to the interpretation of DUNHAM-BUSH, the unit nameplate shall prevail. | [8 empty] | 4.The above parameters are subject to the interpretation of DUNHAM-BUSH, the unit nameplate shall prevail.
Accessories for ACCS+EB unit
DOL starter |  |  | (Y/N/O) | Y
English language control system |  |  | (Y/N/O) | Y
Nylon Filter |  |  | (Y/N/O) | Y
BMS - Modbus RTU RS485 |  |  | (Y/N/O) | Y
UVR/Phase Failure Protect |  |  | (Y/N/O) | Y
IP55 Control panel |  |  | (Y/N/O) | O
7'' Touch screen |  |  | (Y/N/O) | O
Service Valve |  |  | (Y/N/O) | O
Indicating Lights |  |  | (Y/N/O) | O
Filter drier＆Sight glass |  |  | (Y/N/O) | O
Hot water coil |  |  | (Y/N/O) | O
Pressure Gauges for Suc/Disc |  |  | (Y/N/O) | O
Replaceable Core Filter Drier |  |  | (Y/N/O) | O
Electric Heater |  |  | (Y/N/O) | O
Condenser Coil Guard |  |  | (Y/N/O) | O
Low Ambient Kit-1 Cooling 0℃ |  |  | (Y/N/O) | O
Low Ambient Kit-2 Cooling -10℃ |  |  | (Y/N/O) | O
Evaporator Blower Isolator |  |  | (Y/N/O) | O
Fire Interlock connector |  |  | (Y/N/O) | O
G2 Air filter |  |  | (Y/N/O) | O
EEV |  |  | (Y/N/O) | O
Blower flow switch |  |  | (Y/N/O) | O
Belt guard for pully drive blower |  |  | (Y/N/O) | O
Refrigerant Rre-charge |  |  | (Y/N/O) | N

## ACCS-VEB
Parameter sheet of Air-cooled split system-Vertical evaporator blower
DB Model | Cooling capacity | Heating capacity | Supply air flowrate |  | DB Model | Cooling capacity | Heating capacity | Supply air flowrate
| kW | kW | m³/h |  |  | kW | kW | m³/h
ACCS09-HP | 8.6 | 9.3 | 1500 |  | ACCS71-HP | 66.7 | 84.7 | 11600
ACCS09 |  | 一 |  |  | ACCS71 |  | 一
ACCS14-HP | 14.5 | 15.7 | 2400 |  | ACCS80-HP | 79.6 | 95.5 | 13000
ACCS14 |  | 一 |  |  | ACCS80 |  | 一
ACCS17-HP | 17.4 | 18.8 | 3300 |  | ACCS90-HP | 90 | 108 | 15000
ACCS17 |  | 一 |  |  | ACCS90 |  | 一
ACCS28-HP | 27.3 | 31.1 | 4300 |  | ACCS105-HP | 104.9 | 125 | 17500
ACCS28 |  | 一 |  |  | ACCS105 |  | 一
ACCS36-HP | 35.3 | 40.1 | 5500 |  | ACCS140-HP | 139.2 | 169.4 | 23000
ACCS36 |  | 一 |  |  | ACCS140 |  | 一
ACCS40-HP | 39.8 | 45.2 | 6200 |  | ACCS166-HP | 166.4 | 191 | 26000
ACCS40 |  | 一 |  |  | ACCS166 |  | 一
ACCS51-HP | 50.6 | 57.4 | 8000 |  | ACCS180-HP | 180.1 | 216 | 30000
ACCS51 |  | 一 |  |  | ACCS180 |  | 一
ACCS57-HP | 56.8 | 63.4 | 8800 |  | ACCS210-HP | 209.9 | 250 | 35000
ACCS57 |  | 一 |  |  | ACCS210 |  | 一
Notes：1.The cooling capacity is measured under the conditions of nominal air volume, with indoor DB/WB 27/19℃ and outdoor DB/WB 35/24℃;
2.The heating capacity is measured under the conditions of nominal air volume, with indoor DB/WB 20/15℃ and outdoor DB/WB 7/6℃;
3.The above parameters are subject to the interpretation of DUNHAM-BUSH, the unit nameplate shall prevail.
Accessories for ACCS+EB unit
DOL starter |  |  | (Y/N/O) | Y
English language control system |  |  | (Y/N/O) | Y
Nylon Filter |  |  | (Y/N/O) | Y
BMS - Modbus RTU RS485 |  |  | (Y/N/O) | Y
UVR/Phase Failure Protect |  |  | (Y/N/O) | Y
IP55 Control panel |  |  | (Y/N/O) | O
7'' Touch screen |  |  | (Y/N/O) | O
Service Valve |  |  | (Y/N/O) | O
Indicating Lights |  |  | (Y/N/O) | O
Filter drier＆Sight glass |  |  | (Y/N/O) | O
Hot water coil |  |  | (Y/N/O) | O
Pressure Gauges for Suc/Disc |  |  | (Y/N/O) | O
Replaceable Core Filter Drier |  |  | (Y/N/O) | O
Electric Heater |  |  | (Y/N/O) | O
Condenser Coil Guard |  |  | (Y/N/O) | O
Low Ambient Kit-1 Cooling 0℃ |  |  | (Y/N/O) | O
Low Ambient Kit-2 Cooling -10℃ |  |  | (Y/N/O) | O
Evaporator Blower Isolator |  |  | (Y/N/O) | O
Fire Interlock connector |  |  | (Y/N/O) | O
G2 Air filter |  |  | (Y/N/O) | O
EEV |  |  | (Y/N/O) | O
Blower flow switch |  |  | (Y/N/O) | O
Belt guard for pully drive blower |  |  | (Y/N/O) | O
Refrigerant Rre-charge |  |  | (Y/N/O) | N

## ACPS
Parameter sheet of Roof top unit
DB Model |  |  | ACPS*09-HP | ACPS*11-HP | ACPS*13-HP | ACPS*18-HP | ACPS*20-HP | ACPS*23-HP | ACPS*26-HP | DB Model |  |  | ACPS*28-HP | ACPS*30-HP | ACPS*32-HP | ACPS*36-HP | ACPS*42-HP | ACPS*48-HP | ACPS*55-HP | ACPS*64-HP | DB Model |  |  | ACPS*72-HP | ACPS*88-HP | ACPS*104-HP | ACPS*120-HP | ACPS*140-HP | ACPS*170-HP | ACPS*190-HP | ACPS*220-HP
|  |  | ACPS*09 | ACPS*11Z | ACPS*13 | ACPS*18 | ACPS*20 | ACPS*23 | ACPS*26 |  |  |  | ACPS*28 | ACPS*30 | ACPS*32 | ACPS*36 | ACPS*42 | ACPS*48 | ACPS*55 | ACPS*64 |  |  |  | ACPS*72 | ACPS*88 | ACPS*104 | ACPS*120 | ACPS*140 | ACPS*170 | ACPS*190 | ACPS*220
Nominal cooling capacity |  | kW | 8.6 | 10.6 | 12.6 | 17.6 | 19.6 | 23.3 | 25.6 | Nominal cooling capacity |  | kW | 28.8 | 29.9 | 32.4 | 35.6 | 41.6 | 47.2 | 53.2 | 63.3 | Nominal cooling capacity |  | kW | 71.4 | 87.2 | 103.1 | 118.8 | 140.7 | 169.8 | 188.5 | 226.8
Nominal heating capacity |  | kW | 9.3 | 11.3 | 13.4 | 18.8 | 21.3 | 24.9 | 27.7 | Nominal heating capacity |  | kW | 31.1 | 32.3 | 34.6 | 38 | 44.6 | 50.2 | 56.4 | 67 | Nominal heating capacity |  | kW | 75.6 | 93.3 | 109.5 | 126.8 | 152.9 | 179.9 | 203.6 | 242.7
Power supply |  |  | 380V/3Ph/50Hz | [6 empty] | Power supply |  |  | 380V/3Ph/5OHz | [7 empty] | Power supply |  |  | 380V/3Ph/50Hz
Cooling input power |  | kW | 3.46 | 3.97 | 4.86 | 6.49 | 7.68 | 8.38 | 8.9 | Cooling input power |  | kW | 11.03 | 11.6 | 12.4 | 13.14 | 14.8 | 16.97 | 19 | 22.21 | Cooling input power |  | kW | 27.25 | 32.06 | 38.9 | 46.22 | 53.3 | 64 | 70.8 | 85.4
Heating input power |  | kW | 3.2 | 3.63 | 4.47 | 5.89 | 7.07 | 7.8 | 8.29 | Heating input power |  | kW | 10.4 | 10.8 | 11.57 | 12.03 | 13.76 | 15.79 | 17.4 | 19.88 | Heating input power |  | kW | 24.8 | 28.79 | 35.32 | 42.83 | 49.4 | 56.9 | 64.5 | 78.9
Inrush current |  | A | 42 | 48 | 55 | 66 | 47.5 | 54.5 | 61.5 | Inrush current |  | A | 62.5 | 62.9 | 59.9 | 75.3 | 87.9 | 103.9 | 108 | 111.4 | Inrush current |  | A | 114.2 | 154.1 | 197.7 | 160.5 | 166.2 | 183.4 | 192.3 | 243.1
Cooling running current |  | A | 6.5 | 7.2 | 8.1 | 9.8 | 12.2 | 13.6 | 15.1 | Cooling running current |  | A | 17 | 18.5 | 19.6 | 23.1 | 27.9 | 30.9 | 33.7 | 39 | Cooling running current |  | A | 48.3 | 55.6 | 69.7 | 86.5 | 90.9 | 105.7 | 116 | 142.7
Heating running current |  | A | 6.1 | 6.7 | 7.5 | 9.1 | 11.5 | 12.5 | 14 | Heating running current |  | A | 15.6 | 17.2 | 17.8 | 21.6 | 26.1 | 28.7 | 31.3 | 36.5 | Heating running current |  | A | 44.9 | 52.7 | 66.6 | 82 | 86.2 | 100.5 | 111 | 136.1
Throttle type |  |  | Thermostatic expansion valve | [6 empty] | Throttle type |  |  | Thermostatic expansion valve | [7 empty] | Throttle type |  |  | Thermostatic expansion valve
Refrigerant circuit |  |  | 1 |  |  |  | 2 |  |  | Refrigerant circuit |  |  | 1 |  |  |  | 2 |  |  |  | Refrigerant circuit |  |  | 2 |  |  | 4
Refrigerant gas |  |  | R410a/R407c | [6 empty] | Refrigerant gas |  |  | R410a/R407c | [7 empty] | Refrigerant gas |  |  | R410a/R407c
Compressor | Type |  | Scroll | [6 empty] | Compressor | Type |  | Scroll | [7 empty] | Compressor | Type |  | Scroll
| Qty. |  | 1 |  |  |  | 2 |  |  |  | Qty. |  | 1 |  |  |  | 2 |  |  |  |  | Qty. |  | 2 |  |  | 4
Condenser | Type |  | Copper tube & Aluminum fins | [6 empty] | Condenser | Type |  | Copper tube & Aluminum fins | [7 empty] | Condenser | Type |  | Copper tube & Aluminum fins
| Rows/Fins per inch |  | 2/15.88 | 3/12.7 | 3/14 | 2/15.88 | 3/14 | 3/15.88 | 3/15.88 |  | Rows/Fins per inch |  | 3/15.88 | 3/14 | 3/15.88 | 3/14 | 3/12.7 | 3/15.88 | 2025-03-14 | 3/12.7 |  | Rows/Fins per inch |  | 3/12.7 | 3/14 | 3/12.7 | 3/14 | 3/14 | 4/12.7 | 4/14 | 4/14
| Face area | m² | 0.825 | 0.825 | 0.825 | 1.125 | 1.125 | 1.125 | 1.44 |  | Face area | m² | 1.44 | 1.8 | 1.8 | 1.98 | 2.47 | 2.47 | 2.984 | 2.77 |  | Face area | m² | 4.68 | 4.68 | 6.44 | 6.44 | 7 | 7 | 7 | 7
Condenser fan | Power supply |  | 380V/3Ph/50Hz | [6 empty] | Condenser fan | Power supply |  | 380V/3Ph/5OHz | [7 empty] | Condenser fan | Power supply |  | 380-415V/3Ph/50Hz
| Qty. |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | Qty. |  | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 |  | Qty. |  | 2 | 2 | 2 | 4 | 4 | 4 | 4 | 4
| RPM | r/min | 695 | 695 | 965 | 965 | 710 | 710 | 920 |  | RPM | r/min | 920 | 710 | 940 | 720 | 920 | 920 | 920 | 720 |  | RPM | r/min | 720 | 720 | 710 | 940 | 940 | 720 | 720 | 720
| Drive type |  | Direct drive | [7 empty] | Drive type |  | Direct drive | [8 empty] | Drive type |  | Direct drive
| Moter power | kw | 0.15 | 0.15 | 0.25 | 0.37 | 0.37 | 0.45 | 0.55 |  | Moter power | kw | 0.55 | 0.55 | 0.55 | 2x0.37 | 2×0.45 | 2×0.55 | 2x0.55 | 2×0.75 |  | Moter power | kw | 2x0.85 | 2x1.5 | 2x¹.5 | 4x0.75 | 4×0.75 | 4×1.5 | 4x1.5 | 4x1.5
| Air flowrate | m³/h | 3960 | 3780 | 5500 | 7200 | 8640 | 8640 | 9400 |  | Air flowrate | m³/h | 12300 | 12300 | 12300 | 14200 | 18800 | 18800 | 21400 | 28400 |  | Air flowrate | m³/h | 28400 | 42000 | 42000 | 56800 | 56800 | 84000 | 84000 | 84000
Evaporator | Type |  | Copper tube & Aluminum fins | [6 empty] | Evaporator | Type |  | Copper tube & Aluminum fins | [7 empty] | Evaporator | Type |  | Copper tube & Aluminum fins
| Rows/Fins per inch |  | 3/12.7 | 4/12.7 | [6 empty] | Rows/Fins per inch |  | 4/12.7 |  |  | 3/12.7 | 4/12.7 |  |  |  |  | Rows/Fins per inch |  | 4/12.7
| Face area m² |  | 0.28 | 0.28 | 0.28 | 0.46 | 0.51 | 0.6 | 0.6 |  | Face area m² |  | 0.607 | 0.633 | 0.732 | 0.952 | 0.95 | 1.08 | 1.174 | 1.41 |  | Face area m² |  | 1.7 | 1.95 | 2.21 | 2.52 | 2.573 | 3.35 | 3.77 | 4.09
Evaporator blower | Power supply |  | 220V/1Ph/50Hz |  |  |  | 380V/3Ph/50Hz |  |  | Evaporator blower | Power supply |  | 380V/3Ph/50Hz | [7 empty] | Evaporator blower | Power supply |  | 380V3Ph/50Hz
| Qty. |  | 1 | [7 empty] | Qty. |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | Qty. |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| RPM | r/min | 1440/1245 | 1430/1400/1360 |  | 1380/1250 | 1280 |  | 1320 |  | RPM | r/min | 1320 | 1400 | 1120 | 940 | 940 | 1000 | 750 | 750 |  | RPM | r/min | 850 | 850 | 900 | 800 | 800 | 800 | 850 | 740
| Moter power | kw | 0.5 | 0.5 | 0.5 | 0.7 | 0.8 | 0.8 | 1.1 |  | Moter power | kw | 1.1 | 1.5 | 1.5 | 2.2 | 2.2 | 3 | 3 | 4 |  | Moter power | kw | 4 | 4 | 5.5 | 7.5 | 7.5 | 7.5 | 11 | 15
| Air flowrate | m³/h | 1800 | 2120 | 2520 | 2920 | 3600 | 4250 | 4740 |  | Air flowrate | m³/h | 4700 | 5400 | 6300 | 6800 | 7900 | 9360 | 10440 | 12670 |  | Air flowrate | m³/h | 14400 | 16560 | 19440 | 22000 | 26030 | 31400 | 34900 | 42000
| Drive type |  | Direct drive | [7 empty] | Drive type |  | Pully drive | [8 empty] | Drive type |  | Pully drive
External residual pressure |  | Pa | 160 | 150 | 150 | 180 | 170 | 150 | 255 | External residual pressure |  | Pa | 235 | 305 | 290 | 270 | 250 | 290 | 280 | 255 | External residual pressure |  | Pa | 380 | 345 | 390 | 545 | 530 | 420 | 420 | 430
Air filter |  |  | Nylon mesh | [6 empty] | Air filter |  |  | Nylon mesh | [7 empty] | Air filter |  |  | Nylon mesh
Noise |  | dB(A) | 67 | 67 | 68 | 71.7 | 72.6 | 72.6 | 70 | Noise |  | dB(A) | 70 | 72 | 72 | 72 | 72 | 75 | 73 | 73 | Noise |  | dB(A) | 75 | 75 | 75 | 80 | 80 | 80 | 82 | 82.5
Refrigerant charge amount |  | kg | 2.3 | 3.1 | 3.1 | 5.3 | 6 | 6.5 | 6.5 | Refrigerant charge amount |  | kg | 7 | 8.2 | 9 | 2×5.3 | 8+4.2 | 9+4.2 | 10.5+4.2 | 2x9 | Refrigerant charge amount |  | kg | 2×10 | 2×11.5 | 2×13.5 | 2×16 | 2x18 | 2x21.5 | 2×23 | 2x27
Outline dimension | Length | mm | 1280 | 1280 | 1280 | 1660 | 1780 | 1780 | 1940 | Outline dimension | Length | mm | 1940 | 2240 | 2240 | 2540 | 2540 | 2540 | 2490 | 2490 | Outline dimension | Length | mm | 2840 | 2840 | 3410 | 4700 | 5200 | 5500 | 5800 | 5880
| Width | mm | 1040 | 1040 | 1040 | 1040 | 1390 | 1390 | 1390 |  | Width | mm | 1390 | 1390 | 1390 | 1860 | 1860 | 1860 | 2050 | 2210 |  | Width | mm | 2210 | 2210 | 2210 | 2230 | 2230 | 2230 | 2230 | 2230
| Height | mm | 875 | 875 | 875 | 1045 | 1045 | 1045 | 1045 |  | Height | mm | 1045 | 1045 | 1045 | 1045 | 1195 | 1195 | 1390 | 1490 |  | Height | mm | 1510 | 1685 | 1810 | 1640 | 1640 | 1810 | 1810 | 2010
Shipping weight |  | kg | 240 | 245 | 255 | 360 | 400 | 420 | 450 | Shipping weight |  | kg | 460 | 500 | 520 | 650 | 755 | 770 | 810 | 890 | Shipping weight |  | kg | 980 | 1160 | 1450 | 1910 | 2010 | 2280 | 2460 | 2530
Notes：1.The cooling capacity is measured under the conditions of nominal air volume, with indoor DB/WB 27/19℃ and outdoor DB/WB 35/24℃; | [9 empty] | Notes：1.The cooling capacity is measured under the conditions of nominal air volume, with indoor DB/WB 27/19℃ and outdoor DB/WB 35/24℃; | [10 empty] | Notes：1.The cooling capacity is measured under the conditions of nominal air volume, with indoor DB/WB 27/19℃ and outdoor DB/WB 35/24℃;
2.The heating capacity is measured under the conditions of nominal air volume, with indoor DB/WB 20/15℃ and outdoor DB/WB 7/6℃; | [9 empty] | 2.The heating capacity is measured under the conditions of nominal air volume, with indoor DB/WB 20/15℃ and outdoor DB/WB 7/6℃; | [10 empty] | 2.The heating capacity is measured under the conditions of nominal air volume, with indoor DB/WB 20/15℃ and outdoor DB/WB 7/6℃;
3.The above parameters are subject to the interpretation of DUNHAM-BUSH, the unit nameplate shall prevail. | [9 empty] | 3.The above parameters are subject to the interpretation of DUNHAM-BUSH, the unit nameplate shall prevail. | [10 empty] | 3.The above parameters are subject to the interpretation of DUNHAM-BUSH, the unit nameplate shall prevail.
Accessories for ACPS unit
DOL starter |  |  | (Y/N/O) | Y
English language control system |  |  | (Y/N/O) | Y
Nylon Filter |  |  | (Y/N/O) | Y
BMS - Modbus RTU RS485 |  |  | (Y/N/O) | Y
UVR/Phase Failure Protect |  |  | (Y/N/O) | Y
IP55 Control panel |  |  | (Y/N/O) | O
7'' Touch screen |  |  | (Y/N/O) | O
Service Valve |  |  | (Y/N/O) | O
Pressure Gauges for Suc/Disc |  |  | (Y/N/O) | O
Replaceable Core Filter Drier |  |  | (Y/N/O) | O
Electric Heater |  |  | (Y/N/O) | O
Condenser Coil Guard |  |  | (Y/N/O) | O
Low Ambient Kit-1 Cooling 0℃ |  |  | (Y/N/O) | O
Low Ambient Kit-2 Cooling -10℃ |  |  | (Y/N/O) | O
Evaporator Blower Isolator |  |  | (Y/N/O) | O
Fire Interlock connector |  |  | (Y/N/O) | O
G2 Air filter |  |  | (Y/N/O) | O
Hot water coil |  |  | (Y/N/O) | O
EEV |  |  | (Y/N/O) | O
Blower flow switch |  |  | (Y/N/O) | O
Belt guard for pully drive blower |  |  | (Y/N/O) | O
Refrigerant Pre-charge |  |  | (Y/N/O) | N