# AIRDRY

Adsorption Dehumidifiers

TECHNICAL DATA

MODE

L	AD

300

0	35

00	4

500T

4000

5000

Performance

s

Dehumidification Capacity

*	Kg/h

23

2

7,3

21,1

31,7

37,2

Fan

s

Process air flo

w	m3/h

300

0	35

00

4500

4000

5000

Static pressur

e	Pa

400

3

0

300

400

400

Fan nominal pow

er	KW

1,65

1,

65

2,4

2,2

2,2

Reactivation air flo

w	m3/h

900

11

00

900

1350

1600

Static pressur

e	Pa

200

3

0

300

400

350

Fan nominal pow

er	KW

0,49

0,

72

0,72

0,75

1,1

Drive Moto

r

Nominal pow

er	W

10

1

0

10

10

10

Regeneratio

n

Regeneration typ

e

Electr

ic	Ele

ctric	E

lectric

Electric

Electric

Installed pow

er	KW

30,0

3

6,0

27,0

45,0

54,0

Regeneration typ

e

Stea

m	Ste

am

Steam

Steam

Steam

Power output heatin

g	KW

31,1

3

7,9

31,1

46,6

55,2

Steam consuption at 6Bar(

a)	Kg/h

54

6

5

54

80

95

TECNOFRIGO TUSCANY srl

Via J.F.Kennedy, 25-27-29

56020 Capanne (Pisa)

+39 0571 467351

| TECHNICAL DATA |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| MODEL | AD | 3000 | 3500 | 4500T | 4000 | 5000 | 6500T |
| Performances |  |  |  |  |  |  |  |
| Dehumidification Capacity * | Kg/h | 23 | 27,3 | 21,1 | 31,7 | 37,2 | 27,1 |
| Fans |  |  |  |  |  |  |  |
| Process air flow | m3/h | 3000 | 3500 | 4500 | 4000 | 5000 | 6500 |
| Static pressure | Pa | 400 | 350 | 5 300 | 400 | 400 | 400 |
| Fan nominal power | KW | 1,65 | 1,65 | 2,4 | 2,2 | 2,2 | 4,0 |
| Reactivation air flow | m3/h | 900 | 1100 | 900 | 1350 | 1600 | 1100 |
| Static pressure | Pa | 200 | 300 | 0 300 | 400 | 350 | 400 |
| Fan nominal power | KW | 0,49 | 0,72 | 0,72 | 0,75 | 1,1 | 0,75 |
| Drive Motor |  |  |  |  |  |  |  |
| Nominal power | W | 11 | 11 | 10 | 10 | 10 | 10 |
| Regeneration |  |  |  |  |  |  |  |
| Regeneration type |  | Elettrica | Elettrica | Elettrica | Elettrica | Elettrica | Elettrica |
| Installed power | KW | 30,0 | 36,0 | 27,0 | 45,0 | 54,0 | 36,0 |
| Regeneration type |  | Vapore | Vapore | Vapore | Vapore | Vapore | Vapore |
| Power output heating | KW | 31,1 | 37,9 | 31,1 | 46,6 | 55,2 | 37,9 |
| Steam consuption at 6Bar(a) | Kg/h | 54 | 65 | 54 | 80 | 95 | 65 |
| Temperature rise in the heating coil | °C | 100 | 100 | 0 100 | 100 | 100 | 100 |
| Electrical characteristics |  |  |  |  |  |  |  |
| Power supply | Volt/Ph/Hz | 400/3/50 ±5% | 400/3/50 ±5% | 400/3/50 ±5% | 400/3/50 ±5% | 400/3/50 ±5% | 400/3/50 ±5% |
| Maximum power absorbed standard units | KW | 32,3 | 38,5 | 30,3 | 48,1 | 57,5 | 40,9 |
| Maximum current absorbed standard units | A | 46,7 | 55,8 | 43,7 | 69,5 | 83,1 | 60,8 |
| Noise level |  |  |  |  |  |  |  |
| Sound pressure ** | dB (A) | 68 | 68 | 69 | 70 | 72 | 73 |
| Sound power ** | dB (A) | 96 | 96 | 97 | 98 | 100 | 101 |

Temperature rise in the heating co

il	°C

100

1

0

100

100

100

Electrical characteristic

s

Power suppl

y	Volt/Ph/

Hz	400/3/50

±5%	400/3/

50 ±5%	400/

3/50 ±5%	40

0/3/50 ±5%

400/3/50 ±5%

Maximum power absorbed standard unit

s	KW

32,3

3

8,5

30,3

48,1

57,5

Maximum current absorbed standard unit

s	A

46,7

5

5,8

43,7

69,5

83,1

Noise lev

el

Sound pressure *

*	dB (A)

68

6

8

69

70

72

Sound power *

*	dB (A)

96

9

6

97

98

100

* Conditions at 20°C 60% RH

** Sound pressure level calculated in free field, 10 meters from unit, direction factor Q = 2, according to ISO 9614

## DEHUMIDIFICATION CAPACITY

Approximate capacity in Kg/h with different relative humidity values of inlet process air (RH%).

WWW.TFTDRYAIR.COM INFO@TFTDRYAIR.COM

CEN3065 issuance 02.19 Subject to change without notice

# PRINCIPLE OF OPERATION

The dehumidifier works using two air flows; the main one is the air to be dehumidified, while a second flow - of lower flow rate - is used to regenerate the dehumidification rotor. Two fans inside the dehumidifier create these two air flows that cross the rotor in opposi- te directions. The air to be dehumidified, also called "process air", passes through the desiccant rotor impregnated with silica gel. Silica gel is a highly hygroscopic material that absorbs water vapour from the air. As it passes through the rotor, the air transfers its moisture content to the rotor itself. The dehumidified air is then sent to the production room or process to be dehumidified. The dehumidification process can take place between -30°C and +40°C. During the process, the rotor rotates very slowly and is equip- ped with a drive system with a reduction gear and belt. The so-called "regeneration air", is used by the system to remove the absorbed moisture and take it outside: it is heated by a battery inside the dehumidifier, up to about +100°C and crosses the rotor in the opposite direction to the process air and submits it to a reverse process, for which the rotor gives up its moisture content and is restored to its initial absorption capacity. The regeneration air is expelled warm and humid and must be sent outside the treated envi- ronment.

# STRUCTURE

The structure of the dehumidifier is made of painted galvanized steel and/or AISI304 steel with sandwich panels. The upper panel can be removed for maintenance of the electrical components, while to access all the internal mechanical parts just remove the front panel. The connections to the dehumi- difier can be made with standard spiral channels.

# FANS

Fans are directly coupled to single-phase or three-phase motors rated at IP55, ISO F, class B. They are accessible for maintenance by removing a second internal panel so that in operation risk of injury is mitigated. The fans can be controlled by an optional frequency converter to control rotation speed and match performance with specific requirements. As standard, the process fan is set at fixed speed, but it can be configured to run at variable speeds from an external signal, or pressure sensor.

# ROTOR

The dehumidifier has a rotor made of desiccant material. The rotor has an alveolar structure made of heat-resistant corrugated sheets containing the silica gel desiccant material, which creates a high number of axial fluid threads and at the same time a high absorption surface in a small volume. The rotor is constructed to withstand saturated air without being damaged, so it can be coupled with a pre-cooling coil. Furthermore, the rotor is not dama- ged if the process or regeneration fan should stop due to a fault during operation. The rotor is non-combustible and non-flammable.

# TRANSMISSION SYSTEM

A belt drive system controls the movement of the rotor. The belt carries out its traction action on the outer edge of the rotor and is driven by a pulley on the gear motor. A special device maintains the correct tension of the belt to prevent slippage of the belt itself. The correct direction of rotation and tran- smission can be checked by opening the front panel. The rotor is equipped with ball bearings. The rotor shaft is made of steel.

# REGENERATION AIR HEATING COIL

Electrical. The electric regeneration battery has steel elements, connected in a star and divided into 2, 3 or more groups for  step  reg ulation with sequential insertion to have a power modulation. On request, continuous modulation (PWM) with proportional power control can be used to increa- se dehumidifier field efficiency and save energy.

Steam. The steam regeneration battery is built with stainless steel tubes304 and aluminium fins (versions with other materials can be reque- sted as an option), and includes a 2-way valve (supplied as an option) with modulating servomotor, to ensure greater efficiency of the dehumidifier's output, acting on the steam flow rate.

# FILTERS

The dehumidifier has two separate G4 filters: one on the process air inlet and the other on the high temperature regeneration air inlet. On request, hi- gher grade filters can be supplied.

# PLC CONTROL WITH TOUCH-SCREEN TERMINAL

All standard units are supplied with PLC control and touch-screen terminal. The PLC controls the following functions: regeneration temperature control, thermal protection, post-cooling regeneration timing, component start sequence, alarm reset, moisture dehumidification/humidification control, pre- and post-cooling/heating control. The display for the user interface can be remotely controlled. The PLC is set up for step management from an external humidistat, and accepts analogue signals from humidity sensors. On request, the microprocessor can be connected to remote BMS control systems.

The technical department is available to study, together with the customer, different solutions using MODBUS protocols.

# ELECTRICAL PANEL

The electrical panel is manufactured in compliance with European standards 73/23 and 89/336. The electrical panel is accessible from the front of the unit by means of a special key for opening. The following components are installed in all the units as standard: main switch, thermal magnetic switches (to protect the fans and the electrical resistances), fan relays, gearmotor relays, electrical resistance relays (if present). The panel is also equipped with a terminal board with dry contacts for remote ON OFF control and dry contacts for general alarm.

M

odel	AD

30

0	3

500

4500T

4000

5000

A	mm

15

0	1

500

1500

1895

1895

B	mm

10

0	1

020

1020

1115

1115

C	mm

13

5	1

395

1395

1500

1500

Empty we

ight	Kg

35

0	3

60

360

490

530

Connectio

ns

Process air i

nlet	mm

825 x

500	825

x 500	8

25 x 500

800 x 520

800 x 520

Dry air o

utlet	mm

825 x

500	825

x 500	8

25 x 500

800 x 520

800 x 520

Reactivation air i

nlet	mm

355 x

290	355

x 290	3

55 x 290

415 x 350

415 x 350

Wet air o

utlet	mm

Ø 2

80	Ø

280

Ø 280

Ø 315

Ø 315

TECNOFRIGO TUSCANY srl

Via J.F.Kennedy, 25-27-29

56020 Capanne (Pisa)

+39 0571 467351

WWW.TFTDRYAIR.COM INFO@TFTDRYAIR.COM

CEN3065 issuance 02.19 Subject to change without notice

# VERSIONS

AD…	Standard

AD…/TX	Version with external satin stainless steel frame 304

AD…/TTX	Version with steel frame completely inox304 interior and exterior satin AD…/STC	Construction version, with pivoting wheels

Purge area for low Dew Point

Recovery regeneration heat

RCFX

-

○	○	○	○	○

AD Model

Code

3000

3500

45

0T

4000

5000

Painted steel frame

●

●

●

●

●

Satin stainless steel frame 304

TX

○

○

○

○

○

Frame totally stainless steel304 and satin finish outside

TTX

○

○

○

○

○

Construction site version with pivoting wheels

STC

○

○

○

○

○

Frame Handed version

M

○

○

○

○

○

Filters G4 process and reactivation

●

●

●

●

●

Filters F5, F7, F9

○

○

○

○

○

LDP

-

-

-

-

Pre-cooling water coil

W

○

○

○

○

○

Post-cooling water coil

PW

○

○

○

○

○

Post-heating water coil

PHW

○

○

○

○

○

Proportional 3way-valve for pre/post-treatments (supply only)

3WSF

○

○

○

○

○

AD…/M	Handed version (Process and Regeneration airflows are reversed)

| AD Model | Code | 3000 | 3500 | 4500T 0 | 4000 | 5000 | 6500T |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Painted steel frame |  | ● | ● | ● | ● | ● | ● |
| Satin stainless steel frame 304 | TX | ○ | ○ | ○ | ○ | ○ | ○ |
| Frame totally stainless steel304 and satin finish outside | TTX | ○ | ○ | ○ | ○ | ○ | ○ |
| Construction site version with pivoting wheels | STC | ○ | ○ | ○ | ○ | ○ | ○ |
| Frame Handed version | M | ○ | ○ | ○ | ○ | ○ | ○ |
| Filters G4 process and reactivation |  | ● | ● | ● | ● | ● | ● |
| Filters F5, F7, F9 |  | ○ | ○ | ○ | ○ | ○ | ○ |
| Recovery regeneration heat | RCFX | ○ | ○ | ○ | ○ | ○ | ○ |
| Purge area for low Dew Point | LDP | - | - | - | - | - | - |
| Pre-cooling water coil | W | ○ | ○ | ○ | ○ | ○ | ○ |
| Post-cooling water coil | PW | ○ | ○ | ○ | ○ | ○ | ○ |
| Post-heating water coil | PHW | ○ | ○ | ○ | ○ | ○ | ○ |
| Proportional 3way-valve for pre/post-treatments (supply only) | 3WSF | ○ | ○ | ○ | ○ | ○ | ○ |
| Proportional 3way-val. for pre/post-treatments (with assembly) | 3WCM | ○ | ○ | ○ | ○ | ○ | ○ |
| PLC electronic control and touch-screen display |  | ● | ● | ● | ● | ● | ● |
| Remote terminal | TR | ○ | ○ | ○ | ○ | ○ | ○ |
| Different power supply voltage |  | ○ | ○ | ○ | ○ | ○ | ○ |
| Proportional control PWM regenerationheaters | PWM | ○ | ○ | ○ | ○ | ○ | ○ |
| Proportional 2way-valve for steam regeneration | 2VS | ○ | ○ | ○ | ○ | ○ | ○ |
| Process fan inverter (VFD) | VFP | ○ | ○ | ○ | ○ | ○ | ○ |
| Regeneration fan inverter (VFD) | VFR | ○ | ○ | ○ | ○ | ○ | ○ |
| Process filter alarm | ALFP | ○ | ○ | ○ | ○ | ○ | ○ |
| Regeneration filter alarm | ALFR | ○ | ○ | ○ | ○ | ○ | ○ |
| Circular spigot connections for processes/regeneration | CP | ○ | ○ | ○ | ○ | ○ | ○ |
| Temperature sensor / RH%, Absolute Humidity, DewPoint | ST / H | ○ | ○ | ○ | ○ | ○ | ○ |
| Serial RS485 ModBus Interface |  | ● | ● | ● | ● | ● | ● |
| TCP-IP ModBus Interface |  | ● | ● | ● | ● | ● | ● |
| Other protocols and other accessories on request |  | ○ | ○ | ○ | ○ | ○ | ○ |

Process filter alarm

Regeneration fan inverter (VFD)

VFR

○

○	○	○	○	○

Proportional 3way-val. for pre/post-treatments (with assembly)

3WCM

○

○

○

○

○

PLC electronic control and touch-screen display

●

●

●

●

●

Remote terminal

TR

○

○

○

○

○

Different power supply voltage

○

○

○

○

○

Proportional control PWM regenerationheaters

PWM

○

○

○

○

○

Proportional 2way-valve for steam regeneration

2VS

○

○

○

○

○

Process fan inverter (VFD)

VFP

○

○

○

○

○

ALFP

○

○

○

○

Regeneration filter alarm

ALFR

○

○

○

○

○

Circular spigot connections for processes/regeneration

CP

○

○

○

○

○

Temperature sensor / RH%, Absolute Humidity, DewPoint

ST / H

○

○

○

○

○

Serial RS485 ModBus Interface

●

●

●

●

●

TCP-IP ModBus Interface

●

●

●

●

●

Other protocols and other accessories on request

○

○

○

○

○

standard, ○ optional, – not available.

## Dimensions

| Model | AD | 3000 | 0 3500 | 4500T | 4000 | 5000 | 6500T |
| --- | --- | --- | --- | --- | --- | --- | --- |
| A | mm | 1500 | 0 1500 | 1500 | 1895 | 1895 | 1895 |
| B | mm | 1020 | 2 1020 | 1020 | 1115 | 1115 | 1115 |
| C | mm | 1395 | 9 1395 | 1395 | 1500 | 1500 | 1500 |
| Empty weight | Kg | 350 | 360 | 360 | 490 | 530 | 545 |
| Connections |  |  |  |  |  |  |  |
| Process air inlet | mm | 825 x 500 | 825 x 500 | 825 x 500 | 800 x 520 | 800 x 520 | 800 x 520 |
| Dry air outlet | mm | 825 x 500 | 825 x 500 | 825 x 500 | 800 x 520 | 800 x 520 | 800 x 520 |
| Reactivation air inlet | mm | 355 x 290 | 355 x 290 | 355 x 290 | 415 x 350 | 415 x 350 | 415 x 350 |
| Wet air outlet | mm | Ø 280 | Ø 280 | Ø 280 | Ø 315 | Ø 315 | Ø 315 |