## General compatibilty table
General compatibility table, central controllers and gateways per product range | [6 empty] | Last revision | 2023-12-21
System / Product | airCloud Home airCloud Go | Hi-Kumo Wifi | Hi-Kumo Hi-box | Hi-Kumo Pro | CSNET Home | CSNET Manager 2 | airCloud Pro | Central Stations | VRF Modbus Gateway | VRF KNX Gateway | VRF BACnet Gateway | YUTAKI Modbus G/W | YUTAKI KNX Gateway | RAC Modbus Gateway | RAC KNX G/W | PRIMAIRY KNX G/W
Specific device for this control system | Mobile App | Mobile App | AHP-SMB-01 + mobile App | H-K PRO Web App | ATW-IOT-01 + mobile / web App | Software v2.1.2 + CSNET devices | HC-IOTGW + mobile & Web Apps | PSC-A32MN PSC-A64GT | HC-A16MB or HC-A64MB | HI-AC-KNX-16 HI-AC-KNX-64 | HI-AC-BAC-16 HI-AC-BAC-64 | ATW-MBS-02 | ATW-KNX-02 | AZAI6WSCHT2 | AZAI6KNXHT2 | AZAI6KNXHT3
RAC IDU R410A | x | SPX-WFG01 | SPX-TAG01 | SPX-WFG01 or SPX-TAG01 + Hi-box | x | PSC-6RAD | PSC-6RAD (2) mixed with VRF | PSC-6RAD (2) | PSC-6RAD | PSC-6RAD | Yes (1) | x | x | Yes | Yes | x
RAC IDU R32 | SPX-WFG02 | SPX-WFG01 | SPX-TAG01 | SPX-WFG01 or SPX-TAG01 + Hi-box | x | PSC-6RAD (1) | PSC-6RAD (1)(2) mixed with VRF | PSC-6RAD (1)(2) | PSC-6RAD (1) | PSC-6RAD (1) | Yes (1) | x | x | Yes | Yes | x
RAC Multi R32 ODU | x | x | x | x | x | SPX-RAMHLK (1) | SPX-RAMHLK (1)(2) mixed with VRF | SPX-RAMLHK (1)(2) | SPX-RAMHLK (1) | SPX-RAMHLK (1)(3) | SPX-RAMHLK (1)(3) | x | x | x | x | x
RAC airHome IDU 2022 (wall type) | Yes - Built-in adapter | x | SPX-TAG01 | SPX-TAG01 + Hi-box | x | PSC-6RAD | PSC-6RAD (2) mixed with VRF | PSC-6RAD (2) | PSC-6RAD | PSC-6RAD | PSC-6RAD | x | x | Yes | Yes | x
RAC airHome IDU 2024 (duct, cass, floor) | SPX-WFG03 | x | Pending confirmation | [8 empty] | x | x | Yes | Yes | x
YUTAMPO | x | x | ATW-HCD-01 ATW-TAG-02 | ATW-HCD-01 ATW-TAG-02 + Hi-box | ATW-IOT-01 + ATW-HCD-01 (firmware H-0306) | ATW-HCD-01 (6) | x | x | ATW-HCD-01 | x | x | ATW-HCD-01 | ATW-HCD-01 | x | x | x
YUTAKI 2010~2015 | x | x | x | x | x | x | x | x | x | x | x | Direct HLINK | Direct HLINK | x | x | x
YUTAKI 2016~2020 | x | x | ATW-TAG-02 | ATW-TAG-02 + Hi-box | ATW-IOT-01 | Direct HLINK | x | x | Direct HLINK | x | x | Direct HLINK | Direct HLINK | x | x | x
YUTAKI April 21 | x | x | ATW-TAG-02 | ATW-TAG-02 + Hi-box | ATW-IOT-01 | Direct HLINK | x | x | Direct HLINK | x | x | Direct HLINK | Direct HLINK | x | x | x
Cascade controller | x | x | x | x | ATW-IOT-01 (App update required, FY24 TBC) | Direct HLINK | x | x | Direct HLINK | x | x | Direct HLINK | x | x | x | x
VRF / IVx IDU | x | x | x | x | x | Direct HLINK | Direct HLINK | Direct HLINK | Direct HLINK | Direct HLINK | Direct HLINK | x | x | x | x | x
Hydrofree | x | x | x | x | x | Direct HLINK (4) | x | x | Direct HLINK (4) | x | x | Direct HLINK | Direct HLINK | x | x | x
DX KIT & KPI from JCH-ES | x | x | x | x | x | Direct HLINK (5) | Direct HLINK (5) | Direct HLINK (5) | Direct HLINK (5) | Direct HLINK (5) | Direct HLINK (5) | x | x | x | x | x
PRIMAIRY indoor units R410A or R32 with HLINK adapter | SPX-WFG02 + updated HLINK adapter HCAA01NEWI | SPX-WFG01 | SPX-TAG01 | SPX-WFG01 or SPX-TAG01 + Hi-box | x | HCAA01NEWI | Confirmed with updated HLINK adapter HCAA01NEWI | HCAA01NEWI | HCAA01NEWI | HCAA01NEWI | HCAA01NEWI | x | x | x | x | x
PRIMAIRY indoor units R410A or R32 WITHOUT HLINK adapter | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | Yes
Airzone systems | x | x | x | x | x | From CSNET Manager v2.1 | x | x | x | x | x | x | x | x | x | x
Notes
(1): for RAC R32 systems, the connection to HLINK can be done either with PSC-RAD on IDUs or with SPX-RAMHLK on compatible Multi ODUs
(2): RAC systems can be operated from airCloud Pro, with some limitations (refer to the Features & Benefits presentation about airCloud Pro)
The same limitations will be faced with Central Stations (PSC-A32MN and PSC-A64GT)
Update December 2023: airCloud PRO cannot work with an HLINK system made only of RAC adapters (PSC-6RAD or SPX-RAMHLK).
RAC units can be controlled from airCloud PRO ONLY if they are combined with a native HLINK unit (VRF or Utopia/IVX) on their HLINK line.
In case the HLINK line is made only of RAC adapters, airCloud PRO is currently not able to detect the indoor units during the HLINK discovery sequence.
(3): There are some limitations on the current KNX and BACnet gateways with SPX-RAMHLK, the RAC individual controller is always fully locked.
This shall be improved / solved during FY22 by a firmware update of the gateways.
(4):integration of Hydrofree units depends on the Central Controller type: devices from JCH-ES (CSNET Manager, Modbus gateways) are able to
control Hydrofree units as a air-to-water system. Other systems like Central Stations or airCloud Pro will not be able to manage these units,
only the ON/OFF command may be available, without any water data reported.
(5): DX KIT and KPI units from JCH-ES are detected by HLINK central controllers as standard HLINK indoor units. Standard control commands
and parameter status are available for all HLINK central controllers, but some limitations may be faced for the devices not designed by JCH-ES.
Only CSNET Manager is able to display all the specific temperatures of DX KIT and KPI units. All the other devices can at least manage ON/OFF,
operation mode and temperature setting (only with air inlet control for DX KIT).
(6): Yutampo multi systems with ATW-HCD-01 and SPX-RAMHLK HLINK adapters can be used with CSNET Manager, setting a different refrigerant cycle address on Yutampo tank and SPX-RAMHLK, to avoid communication issues. In case of Multi + Yutampo combination on HLINK, PSC-6RAD RAC HLINK adapter can also be used.
References highlighted in red are terminated and may no longer be available on stock: SPX-WFG01, ATW-TAG-02.
Pending confirmation

## HLINK CONTROLLERS TABLE
General combination tables between HLINK individual and central controllers | [9 empty] | Source: Controls technical catalogue, TCBG00125
Devices connected together or combined on the same HLINK | [9 empty] | Last revision |  |  |  |  | 2023-12-20
Individual controllers are connected to the RCS HLINK (A/B terminals)
Central controllers are connected to the central HLINK (1/2 terminals)
|  | PC-ARFG-E | PC-ARFG2-E(B) | PC-ARFP1E | PC-ARH1E | PC-AWR | PSC-A64GT | PSC-A32MN | PSC-A64S | PSC-A16RS | CSNET WEB | airCloud Pro | CSNET Manager 2 | CSNET Lite | HC-A64NET | HC-A16MB | HC-A64MB | KNX001 | HI-AC-BAC-16/64 | HI-AC-KNX-16/64 | HARC-BX E (A) | HARC-BX E (B) | PSC-A1T | PC-A1IO | PC-AIO2 | PSC-5HR(1) | PSC-6RAD | SPX-RAMHLK | HCAA01NEWI
Individual remote controllers | PC-ARFG-E | o | o | o | o | o | o | o | o | o | o | o | o | o | o | o | o | o | o | o | o | o | (2) | - |  | - | - | - | -
| PC-ARFG2-E(B) | o | o | o | o | o | o | o | o | o | o | o | o | o | o | o | o | o | o | o | o | o | (2) | - |  | - | - | - | -
| PC-ARFP1E | o | o | o | o | o | o | o | o | o | o | o | o | o | o | o | o | o | o | o | o | o | (2) | - |  | - | - | - | -
| PC-ARH1E | o | o | o | o | o | o | o | o | o | o | o | o | o | o | o | o | o | o | o | o | o | (2) | - |  | - | - | - | -
| PC-AWR | o | o | o | o | o | o | o | o | o | o | o | o | o | o | o | o | o | o | o | o | o | (2) | - |  | - | - | - | -
Central controllers / Central stations | PSC-A64GT | o | o | o | o | o | o | o | o | o | (1) | o | x | x | x | x | x | x | x | x | x | x | (2) | o | o | o | o | o | o
| PSC-A32MN | o | o | o | o | o | o | o | o | o | (1) | o | x | x | x | x | x | x | x | x | x | x | (2) | o | o | o | o | o | o
| PSC-A64S | o | o | o | o | o | o | o | o | o | (1) | x | x | x | x | x | x | x | x | x | x | x | o | o | o | o | o | x | x
| PSC-A16RS | o | o | o | o | o | o | o | o | o | (1) | x | x | x | x | x | x | x | x | x | x | x | o | o | o | o | o | x | x
Advanced central controllers | CSNET WEB | o | o | o | o | o | (1) | (1) | (1) | (1) | x | x | (1) | (1) | x | x | x | o | x | x | x | x | (2) | o | o | o | o | x | x
| airCloud Pro | o | o | o | o | o | o | o | x | x | x | o | x | x | x | x | x | x | x | x | x | x | (2) | x | x | o | (3) | (3) | o
| CSNET Manager 2 | o | o | o | o | o | x | x | x | x | (1) | x | o | o | o | x | x | (1) | o | o | x | x | (2) | o | o | o | o | o | o
| CSNET Lite | o | o | o | o | o | x | x | x | x | (1) | x | o | o | o | x | x | (1) | o | o | x | x | (2) | o | o | o | o | o | o
| HC-A64NET | o | o | o | o | o | x | x | x | x | x | x | o | o | x | x | x | x | x | x | x | x | - | o | o | o | o | o | o
BMS gateways | HC-A16MB | o | o | o | o | o | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | - | o | o | o | o | o | o
| HC-A64MB | o | o | o | o | o | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | - | o | o | o | o | o | o
| KNX001 | o | o | o | o | o | x | x | x | x | o | x | (1) | (1) | x | x | x | x | x | x | x | x | - | o | o | o | o | x | x
| HI-AC-BAC-16/64 | o | o | o | o | o | x | x | x | x | x | x | o | o | x | x | x | x | x | x | x | x | - | o | o | o | o | (1) | o
| HI-AC-KNX-16/64 | o | o | o | o | o | x | x | x | x | x | x | o | o | x | x | x | x | x | x | x | x | - | o | o | o | o | (1) | o
| HARC-BX E (A) | o | o | o | o | o | x | x | x | x | x | x | x | x | x | x | x | x | x | x | o | o | - | x | x | o | x | x | x
| HARC-BX E (B) | o | o | o | o | o | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | o | - | x | x | o | x | x | x
Additional HLINK devices | PSC-A1T | (2) | (2) | (2) | (2) | (2) | (2) | (2) | o | o | (2) | (2) | (2) | (2) | - | - | - | - | - | - | - | - | x | - | - | o | - | - | -
| PC-A1IO | - | - | - | - | - | o | o | o | o | o | x | o | o | o | o | o | o | o | o | x | x | - | o | o | o | o | o | o
| PC-AIO2 | o | o | o | o | - | o | o | o | o | o | x | o | o | o | o | o | o | o | o | x | x | - | o | o | o | o | o | o
| PSC-5HR(1) | - | - | - | - | - | o | o | o | o | o | o | - | o | o | o | o | o | o | o | o | o | o | o | o | o | o | o | o
RAC to HLINK adapters | PSC-6RAD | - | - | - | - | - | o | o | x | x | o | (3) | o | o | o | o | o | o | o | o | x | x | - | o | o | o | o | x | o
| SPX-RAMHLK | - | - | - | - | - | o | o | x | x | x | (3) | o | o | o | o | o | x | (1) | (1) | x | x | - | o | o | o | x | o | o
PRIMAIRY HLINK adapter | HCAA01NEWI (updated) | - | - | - | - | - | o | o | x | x | x | o | o | o | o | o | o | x | o | o | x | x | - | o | o | o | o | o | o
Notes
In case a compatibility between devices is not sure / not confirmed / not tested, it is indicated as not compatible (x)
'-' : not relevant combination or devices that are not directly combined
'o": compatible devices or devices that can be combined on the same HLINK bus
(1): compatibles devices with some limitations, refer to the dedicated manual or presentation for more details
(2): PSC-A1T is connected directly to a central controller (PSC-A64S). If there are other controls in the same H-LINK II system with timer settings, ensure that contradictory timer orders are not set. The last order sent will have priority.
(3): Update December 2023: airCloud PRO cannot work with an HLINK system made only of RAC adapters (PSC-6RAD or SPX-RAMHLK). RAC units can be controlled from airCloud PRO ONLY if they are combined with a native HLINK unit (VRF or Utopia/IVX) on their HLINK line. In case the HLINK line is made only of RAC adapters, airCloud PRO is currently not able to detect the indoor units during the HLINK discovery sequence.

## IoT summary FY24
|  |  | Last revision | 2023-12-20
|  | Residential applications |  | Commercial applications
PRODUCTS |  | airCloud Go (ex airCLoud Home) | CSNET Home | airCloud Pro | CSNET Manager or CSNET Lite
|  | airCloud Go mobile App for iOS and Android | CSNET Home mobile Apps (iOS & Android) CSNET Home Web App CSNET Home PRO Web App | airCloud Pro mobile App for iOS and Android | CSNET Manager App v2.1.1
RAC Legacy | RAC IDU R410A | SPX-WFG02 | x | PSC-6RAD or SPX-RAMHLK (5) | PSC-6RAD or SPX-RAMHLK (5)
| RAC IDU R32 | SPX-WFG02 | x | PSC-6RAD or SPX-RAMHLK (5) | PSC-6RAD or SPX-RAMHLK (5)
airHome range | airHome 2022 (wall type) | Built-in WiFi adapter | x | PSC-6RAD or SPX-RAMHLK (5) | PSC-6RAD or SPX-RAMHLK (5)
| airHome 2024 (wall type) | Built-in WiFi adapter | x | to be confirmed | to be confirmed
| airHome 2024 (duct, cass, floor) | SPX-WFG03 (1) | x | to be confirmed | to be confirmed
YUTAMPO | YUTAMPO Tank unit | x | ATW-HCD-01 + ATW-IOT-01 (2) | x | ATW-HCD-01
YUTAKI range | YUTAKI 2010~2015 | x | x | x | Direct HLINK connection (6)
| YUTAKI 2016~2020 | x | ATW-IOT-01 | x | Direct HLINK connection
| YUTAKI from 2021 | x | ATW-IOT-01 | x | Direct HLINK connection
| Cascade controller | x | x (3) | x | Direct HLINK connection
PRIMAIRY range | Primairy units R410A or R32 with HLINK adapter | HCAA01NEWI (4) + SPX-WFG02 | x | HCAA01NEWI (4) | HCAA01NEWI (4)
Utopia range | Prime & Ivx | x | x | Direct Hlink connnection | Direct Hlink connnection
Notes
(1): SPX-WFG03 is a new WiFi gateway dedicated to airHome indoor units to be released
in 2024. Similar hardware as SPX-WFG02, with additional safety feature for airHome units.
(2): ATW-HCD-01 has been updated to get the compatibility of Yutampo units with
CSNET Home (firmware version H-0306, applied on production from end september 2023)
(3): CSNET Home system is currently not compatible with Cascade Controller, software
updates are necessary to get this compatibility. This is expected with the next update
of CSNET Home system (version 1.2, time to market to be confirmed).
(4): HCAA01NEW HLINK adapter has been updated begining of 2023 with a new firmware
version to get the compatibility with airCloud Home (airCLoud Go) and airCloud Pro solutions.
JCH-EU stock has been updated with this new firmware. Once this stock will be terminated,
HCAA01NEWI will be replaced by HCAA03NEWI (same device with updated firmware applied
from factory).
(5): Standard RAC indoor units can be connected to HLINK using the adaptor PSC-6RAD (one
adaptor per indoor unit). Multi systems can be connected to HLINK using the multi adaptor
SPX-RAMHLK connected to the Multi Outdoor unit.
The compatibility of the new airHome Multi range with these adaptors has to be confirmed.
(6): Old Yutaki units manufactured between 2010 and 2015 can be connected to CSNET Manager
through the HLINK line if they are updated with the last firmware versions available. Refer
to the APN of CSNET Manager v2.0 for details.
(EG-2020010_r1-CSNET manager software v2.0 revised.pdf, July 2021)

## IoT Multi+Yutampo FY24
Last revision | 2023-12-20
|  |  |  | Residential applications |  | Commercial applications
|  | PRODUCTS |  | airCloud Go (ex airCLoud Home) | CSNET Home | CSNET Manager or CSNET Lite
|  |  |  | airCloud Go mobile App for iOS and Android | CSNET Home mobile Apps (iOS & Android) CSNET Home Web App CSNET Home PRO Web App | CSNET Manager App v2.1.1
|  | Standard Multi + Yutampo | RAC IDU R410A | SPX-WFG02 | x | PSC-6RAD or SPX-RAMHLK (3)
|  |  | RAC IDU R32 | SPX-WFG02 | x | PSC-6RAD or SPX-RAMHLK (3)
|  |  | Yutampo tank | x | ATW-HCD-01 + ATW-IOT-01 (2) | ATW-HCD-01
|  | airHome R32 Multi (2024) + Yutampo | airHome 2024 (wall type) | Built-in WiFi adapter | x | To be confirmed
|  |  | airHome 2024 (duct, cass, floor) | SPX-WFG03 (1) | x | To be confirmed
|  |  | YUTAMPO Tank unit | x | ATW-HCD-01 + ATW-IOT-01 (2) | ATW-HCD-01
Notes:
As of december 2023, the control of Multi + Yutampo systems has to be done using 2 applications:
airCloud Go for the RAC air-to-air units, CSNET Home for the Yutampo Tank.
There is a project to integrate Yutampo in airCloud Go system, but so far this is postponed to 2025.
(1): SPX-WFG03 is a new WiFi gateway dedicated to airHome indoor units to be released
in 2024. Similar hardware as SPX-WFG02, with additional safety feature for airHome units.
(2): ATW-HCD-01 has been updated to get the compatibility of Yutampo units with
CSNET Home (firmware version H-0306, applied on production from end september 2023)
(3): Standard RAC indoor units can be connected to HLINK using the adaptor PSC-6RAD (one
adaptor per indoor unit). Multi systems can be connected to HLINK using the multi adaptor
SPX-RAMHLK connected to the Multi Outdoor unit.
Caution: When SPX-RAMHLK and Yutampo tank (with ATW-HCD-01) are combined on the same HLINK line,
to be controlled by CSNET Manager, a different HLINK Address shall be used for SPX-RAMHLK and
the Yutampo tank, to avoid some communication issues.
The compatibility of the new airHome Multi range with these adaptors has to be confirmed.

## MULTI + YUTAMPO
General compatibility table related to Multi + YUTAMPO systems + Control by EU Central Controllers | [9 empty] | Source: SPX-RAMHLK Features & Benefits June 2021.pptx
[10 empty] | Last revision | 2023-12-21
System | Hi-Kumo (radio) | airCloud Home | CSNET Manager |  | Modbus BMS |  |  | KNX BMS |  |  | BACNET BMS
Availability | Available until end of stock | Already available | Already available | New option from FY21-Q4 | Already available | New option from FY21-Q4 | Available | Already available | Future (FY23 TBC) | Available (FY23-Q1) | Already available | Future (FY23 TBC)
Multi ODU | - | - | - | SPX-RAMHLK (4) | - | SPX-RAMHLK (4) | - | - | SPX-RAMHLK | - | - | SPX-RAMHLK
RAC IDU 1 | SPX-TAG01 | SPX-WFG02 | PSC-6RAD | - | PSC-6RAD | - | AZAI6WSHT2 | PSC-6RAD | - | AZAI6KNXHT2 | PSC-6RAD | -
RAC IDU 2 | SPX-TAG01 | SPX-WFG02 | PSC-6RAD | - | PSC-6RAD | - | AZAI6WSHT2 | PSC-6RAD | - | AZAI6KNXHT2 | PSC-6RAD | -
RAC IDU 3 | SPX-TAG01 | SPX-WFG02 | PSC-6RAD | - | PSC-6RAD | - | AZAI6WSHT2 | PSC-6RAD | - | AZAI6KNXHT2 | PSC-6RAD | -
RAC IDU 4 | SPX-TAG01 | SPX-WFG02 | PSC-6RAD | - | PSC-6RAD | - | AZAI6WSHT2 | PSC-6RAD | - | AZAI6KNXHT2 | PSC-6RAD | -
YUTAMPO | ATW-HCD-01 | Not compatible | ATW-HCD-01 | ATW-HCD-01 (4) | ATW-HCD-01 | ATW-HCD-01 (4) | ATW-HCD-01 | ATW-HCD-01 | ATW-HCD-01 | ATW-HCD-01 | No gateway available | ATW-HCD-01
| ATW-TAG-02 |  | - | - | - | - | ATW-MBS-02 | ATW-KNX-02 | - | ATW-KNX-02 |  | -
Additional interfaces | Hi-box AHP-SMB-01 | - | CSNET device updated to v2.1 | CSNET device updated to v2.1 | HC-A16MB or HC-A64MB | HC-A16MB or HC-A64MB | - | HI-AC-KNX-16 or HI-AC-KNX-64 to manage ATA units | HI-AC-KNX-16 HI-AC-KNX-64 Update pending to be compatible with SPX-RAMHLK and with ATW data | - | HI-AC-BAC-16 or HI-AC-BAC-64 | HI-AC-BAC-16 HI-AC-BAC-64 Update pending to be compatible with SPX-RAMHLK and with ATW data
Comments | - | - | - | - | - | - |  | - | Best option for medium / large systems (more than 10 RAC indoor units) | Best option for small systems (less than 10 units)
Notes:
For Hi-Kumo, it is possible to control all the units (ATA + ATW) from the same user's account (first create the account with Hi-box, then add the devices)
airCloud Home is not compatible with ATW systems. airCloud and Hi-Kumo systems are not compatible
As long as there is stock of Hi-Kumo ATW gateways, the YUTAMPO tank will stay controlable from Hi-Kumo: caution from FY23-Q1 with ATW-TAG-02 that is becoming terminated and no longer available.
One possible solution is to use airCloud Home for ATA units and Hi-Kumo for the water tank (one user's account for airLCoud Home, one account for Hi-Kumo)
Modbus gateways for VRF HC-A16MB and HC-A64MB are able to manage ATA and ATW units from May 2020
Current KNX gateways for VRF HI-AC-KNX-16 / 64 are not fully compatible with SPX-RAMHLK and not managing ATW units.
An update shall be done in FY22 Q1/Q2 to add these compatibilities.
Current VRF BACNET gateways are not compatible with ATW units. Currently it is then not possible to control a Multi + YUTAMPO system from a BACNET BMS.
Only RAC ATA units can be controlled from the BACNET BMS.
An update of the BACNET gateway is pending to add the compatibility with SPX-RAMHLK and with ATW units.
(4): SPX-RAMHLK and ATW-HCD-01:
To ensure a correct operation with CSNET Manager and Modbus gateway HC-A16/64MB, when mixing ATW-HCD-01 and SPX-RAMHLK on the same HLINK line,
it is necessary to set a different refrigerant cycle address on SPX-RAMHLK and Yutampo tank, even if the RAC IDU and the Yutampo tank
are physically on the same RAM outdoor unit. As an example, keep HLINK cycle address 0 for Yutampo and set a different
HLINK cycle address (1, 2…) on SPX-RAMHLK.
If the same HLINK address is set on SPX-RAMHLK and Yutampo, communication issues will be faced on CSNET Manager and Modbus gateway.
PSC-6RAD can also be used on RAC IDU in combination with ATW-HCD-01. In this case, until further clarification, we recommend to also use
different refrigerant cycle addresses for the Yutampo tank and the RAC indoor units (so far, no issues reported about this setting when PSC-6RAD is used).

## SPX-RAMHLK
SPX-RAMHLK: RAC R32 ODU HLINK ADAPTER |  |  | Source: SPX-RAMHLK Features & Benefits June 2021.pptx => revised version December 2023
|  |  | Last revision | 2023-12-20
Combination with HLINK controllers | HLINK Central Controllers |  |  |  | HLINK BMS gateways |  |  | Combination with HLINK controllers | Home Automation |  |  | RAC system
| CSNET Manager 2 | CSNET Lite | airCloud Pro | Central Stations | VRF Modbus Gateway | VRF KNX Gateway | VRF BACnet Gateway |  | airCloud Home | Hi-Kumo Wifi | Hi-Kumo Hi-box | RAC wired controller
Device or gateway reference | CSNET Manager 2T10, 2T15, 2SL HC-A64NET Updated to v2.0 | CSNET Lite Software v2.0 | HC-IOTGW | PSC-A32MN PSC-A64GT | HC-A16MB HC-A64MB | HI-AC-KNX-16 HI-AC-KNX-64 | HI-AC-BAC-16 HI-AC-BAC-64 | Device or gateway reference | SPX-WFG02 | SPX-WFG01 | SPX-TAG01 AHP-SMB-01 | SPX-WKT3 (1 per IU) | SPX-WKT3 + SPX-DST1
Compatibility with Multi HLINK adapter SPX-RAMHLK | Yes (1) | Yes (1) | Yes, combined with a VRF unit (2) | Yes | Yes | Partial, update pending | Partial, update pending | Compatibility with Multi HLINK adapter SPX-RAMHLK | Not recommended (1) | Not recommended (1) | Not recommended (1) | Yes | Not tested & not recommended (2)
Compatibility with SPX-WKT3 (1 per IU) | Yes | Yes | Yes, combined with a VRF unit (2) | Yes | Yes | Partial, update pending | Partial, update pending | Notes:
Combination with airCloud Home or Hi-Kumo | Can work but not recommended | [6 empty] | (1): Combination with iOT gateways can work but is not recommended.
Notes | [7 empty] | RAC indoor unit can follow the orders either from the HLINK system or from the iOT App, the last order submitted will have priority.
(1): CSNET Manager and CSNET Lite can manage RAC units using SPX-RAMHLK adapter IF there is no ATW system using ATW-HCD-01 | [7 empty] | However these are not recommended combinations, as depending on the settings done on the HLINK system to lock parameters,
adapter on the HLINK line. Communication issues between SPX-RAMHLK and ATW-HCD-01 have been detected and shall be solved. | [7 empty] | unexpected behavior of the RAC units may occur.
(2): Update December 2023: airCloud PRO cannot work with an HLINK system made only of RAC adapters (PSC-6RAD or SPX-RAMHLK). RAC units can be controlled from airCloud PRO ONLY if they are combined with a native HLINK unit (VRF or Utopia/IVX) on their HLINK line. In case the HLINK line is made only of RAC adapters, airCloud PRO is currently not able to detect the indoor units during the HLINK discovery sequence. | [7 empty] | It is not recommended to propose such combination to customers.
In case it is required to control RAC units through an App, it is better to propose airCloud PRO.
(2): Combination of HLINK controller through SPX-RAMHLK with SPX-WKT3 and SPX-DST1 has not been tested.
Instead of combining SPX-WKT3+SPX-DST1 + HLINK controller, it is recommended to use only one HLINK controller like PSC-A32MN to control all the RAC units.

## PRIMAIRY HLINK Adapter
PRIMAIRY HLINK Adapter HCAA01NEWI: general compatibility table | [5 empty] | Source: Features & Benefits PRIMAIRY gateway HCAA01NEWI rev1 sept 21.pptx
[6 empty] | Last revision |  | 2023-12-21
| Home Automation |  |  | RAC system | HLINK Central Controllers |  |  | HLINK BMS gateways |  |  |  |  | PRIMAIRY gateway
| airCloud Home | Hi-Kumo Wifi | Hi-Kumo Hi-box | RAC wired controller | CSNET Manager 2 & CSNET Lite | airCloud Pro | Central Stations | VRF Modbus Gateway | VRF KNX Gateway | VRF BACnet Gateway | YUTAKI Modbus G/W | YUTAKI KNX Gateway | KNX Gateway
Specific device for this control system | Mobile App | Mobile App | AHP-SMB-01 + mobile App |  | Software v2.0 + CSNET devices | HC-IOTGW + mobile & Web Apps |  | HC-A16MB or HC-A64MB | HI-AC-KNX-16 HI-AC-KNX-64 | HI-AC-BAC-16 HI-AC-BAC-64 | ATW-MBS-02 | ATW-KNX-02
RAC IDU R410A | x | SPX-WFG01 | SPX-TAG01 |  | PSC-6RAD | PSC-6RAD (2) |  | PSC-6RAD | PSC-6RAD | Yes (1) | x | x
RAC IDU R32 | SPX-WFG02 | SPX-WFG01 | SPX-TAG01 |  | PSC-6RAD (1) | PSC-6RAD (1)(2) |  | PSC-6RAD (1) | PSC-6RAD (1) | Yes (1) | x | x
RAC Multi R32 ODU | x | x | x |  | SPX-RAMHLK (1) | SPX-RAMHLK (1)(2) |  | SPX-RAMHLK (1) | SPX-RAMHLK (1) | SPX-RAMHLK (1) | x | x
YUTAMPO | x | x | ATW-HCD-01 ATW-TAG-02 |  | ATW-HCD-01 | x |  | ATW-HCD-01 | x | x | ATW-HCD-01 | ATW-HCD-01
YUTAKI 2010~2015 | x | x | x |  | x | x |  | x | x | x | Direct HLINK | Direct HLINK
YUTAKI 2016~2020 | x | x | ATW-TAG-02 |  | Direct HLINK | x |  | Direct HLINK | x | x | Direct HLINK | Direct HLINK
YUTAKI April 21 | x | x | ATW-TAG-02 |  | Direct HLINK | x |  | Direct HLINK | x | x | Direct HLINK | Direct HLINK
Cascade controller | x | x | x |  | x | x |  | Direct HLINK | x | x | Direct HLINK | x
VRF / IVx IDU | x | x | x |  | Direct HLINK | Direct HLINK |  | Direct HLINK | Direct HLINK | Direct HLINK | x | x
Hydrofree | x | x | x |  | Direct HLINK | x |  | Direct HLINK | x | x | x | x
Device or gateway reference | SPX-WFG02 | SPX-WFG01 | SPX-TAG01 AHP-SMB-01 | SPX-WKT3 SPX-WKT4 SPX-DST1 | CSNET Manager 2T10, 2T15, 2SL HC-A64NET CSNET Lite | HC-IOTGW | PSC-A32MN PSC-A64GT | HC-A16MB HC-A64MB | HI-AC-KNX-16 HI-AC-KNX-64 | HI-AC-BAC-16 HI-AC-BAC-64 |  |  | AZAI6KNXHT3
Compatibility with Primairy HLINK adapter HCAA01NEWI | Yes (updated HLINK adapter required) | Pending confirmation with udpated HCAA01NEWI adapter | Pending confirmation with udpated HCAA01NEWI adapter | Yes | Yes | Yes (updated HLINK adapter required) | Yes | Yes | Yes | Yes | x | x | X
Compatibility with Hi-Kumo Pro | X | Yes | Yes | X | X | X | X | X | X | X | x | x | X
Notes:
Official Compatibility with airCloud Home is available since February 2023.
airCloud Pro is also compatible with the HLINK adapter HCAA01NEWI since February 2023 (updated HLINK adapter for PRIMAIRY).
Combination of HCAA01NEWI with SPX-WKT3/WKT4 + SPX-DST1 is NOT working and shall not be done (update September 2021).
Available parameters for PRIMAIRY units may change depending on the control system used.
Please refer to the details given in the features and benefits presentation

## PRIMAIRY Wired controller
PRIMAIRY WIRED CONTROLLER HCWA21NEHH: general compatibility |  |  |  | Source: Features & Benefits PRIMAIRY wired controller HCWA21NEHH July 2021.pptx
|  |  |  | Last revision | 2023-12-20
Devices \ Combination | Single PRIMAIRY indoor unit | Several PRIMAIRY units Group Control with HDBA21NEHH | HLINK Adapter HCAA01NEWI (1 adapter per unit) | PRIMAIRY KNX gateway AZAI6KNXHT3
Wired controller HCWA21NEHH | OK | OK | OK | X
Wireless controller | OK | X | OK | OK
HLINK Adapter HCAA01NEWI | OK | X | - | X
Set Back function from HCWA21NEHH | OK | OK | OK | X
Notes:
- Only 1 wired controller HCWA21NEHH can be used per PRIMAIRY unit, for single control, group control and when combined with the HLINK adapter HCAA01NEWI.
- Wireless controller HRBA31NEGH shall not be used when Group Control function is activated from HCWA21NEHH
- HLINK adapter HCAA01NEWI is not compatible with Group Control function from HCWA21NEHH
- Set Back function from wired controller HCWA21NEHH is available for all the combinations (single unit, group control, HLINK control)
- The PRIMAIRY KNX gateway AZAI6KNXHT3 cannot be used in combination with any PRIMAIRY wired controller or with the HLINK adapter HCAA01NEWI
because all these devices are using the same connection port on the IU main PCB (e.g. the wired remote controller port)
- When the wired controller HCWA21NEHH is connected to the HLINK adapter HCAA01NEWI, the Function settings and System parameters cannot be set.
These settings must be made with a direct connection between the wired controller HCWA21NEHH and the main PCB of the indoor unit.