## List1
| Extract air temperature max.##OTHER## | Supply air temperature max.##OTHER## | Temperature of the heating medium max.##OTHER## | Pressure of the heating medium max.##OTHER## | Supply voltage##OTHER## | Permitted voltage tolerance##OTHER## | Frequency##OTHER## | Connected load##OTHER## | Current consumption max.##OTHER## | Series fuse##OTHER## | Protection rating##OTHER## | Nominal air flow rate##HVAC_AIR_FLOW##CUBIC_METERS_PER_HOUR | Floor area covered##AREA##SQUARE_METERS | Static efficiency of the fans##OTHER## | Effective electric power input##OTHER## | Heat output -5/-15 °C (80/60 °C)##OTHER## | Maximum mounting height -5/-15 °C (80/60 °C)##OTHER## | Supply air temperature -5/-15 °C (80/60 °C)##OTHER## | Water pressure drop -5/-15 °C (80/60 °C)##OTHER## | Water quantity -5/-15 °C (80/60 °C)##OTHER## | Heat output -5/-15 °C (60/40 °C)##OTHER## | Maximum mounting height -5/-15 °C (60/40 °C)##OTHER## | Supply air temperature -5/-15 °C (60/40 °C)##OTHER## | Water pressure drop -5/-15 °C (60/40 °C)##OTHER## | Water quantity -5/-15 °C (60/40 °C)##OTHER## | Sound pressure level (at a distance of 5 m)##OTHER## | Total sound power level##OTHER## | Octave sound power level - 63 Hz##OTHER## | Octave sound power level - 125 Hz##OTHER## | Octave sound power level - 250 Hz##OTHER## | Octave sound power level - 500 Hz##OTHER## | Octave sound power level - 1000 Hz##OTHER## | Octave sound power level - 2000 Hz##OTHER## | Octave sound power level - 4000 Hz##OTHER## | Octave sound power level - 8000 Hz##OTHER## | A##LENGTH##MILLIMETERS | F##LENGTH##MILLIMETERS | G##LENGTH##MILLIMETERS | H##LENGTH##MILLIMETERS | I##LENGTH##MILLIMETERS | O##LENGTH##MILLIMETERS | P##LENGTH##MILLIMETERS | K##LENGTH##MILLIMETERS | R##LENGTH##MILLIMETERS | J##LENGTH##MILLIMETERS | Water content of heating coil##OTHER## | Weight##OTHER## | COBIE Extract air temperature max.##OTHER## | COBIE Supply air temperature max.##OTHER## | COBIE Temperature of the heating medium max.##OTHER## | COBIE Pressure of the heating medium max.##OTHER## | COBIE Supply voltage##OTHER## | COBIE Permitted voltage tolerance##OTHER## | COBIE Frequency##OTHER## | COBIE Connected load##OTHER## | COBIE Current consumption max.##OTHER## | COBIE Series fuse##OTHER## | COBIE Protection rating##OTHER## | COBIE Nominal air flow rate##OTHER## | COBIE Floor area covered##OTHER## | COBIE Static efficiency of the fans##OTHER## | COBIE Effective electric power input##OTHER## | COBIE Heat output -5/-15 °C (80/60 °C)##OTHER## | COBIE Maximum mounting height -5/-15 °C (80/60 °C)##OTHER## | COBIE Supply air temperature -5/-15 °C (80/60 °C)##OTHER## | COBIE Water pressure drop -5/-15 °C (80/60 °C)##OTHER## | COBIE Water quantity -5/-15 °C (80/60 °C)##OTHER## | COBIE Heat output -5/-15 °C (60/40 °C)##OTHER## | COBIE Maximum mounting height -5/-15 °C (60/40 °C)##OTHER## | COBIE Supply air temperature -5/-15 °C (60/40 °C)##OTHER## | COBIE Water pressure drop -5/-15 °C (60/40 °C)##OTHER## | COBIE Water quantity -5/-15 °C (60/40 °C)##OTHER## | COBIE Sound pressure level (at a distance of 5 m)##OTHER## | COBIE Total sound power level##OTHER## | COBIE Octave sound power level - 63 Hz##OTHER## | COBIE Octave sound power level - 125 Hz##OTHER## | COBIE Octave sound power level - 250 Hz##OTHER## | COBIE Octave sound power level - 500 Hz##OTHER## | COBIE Octave sound power level - 1000 Hz##OTHER## | COBIE Octave sound power level - 2000 Hz##OTHER## | COBIE Octave sound power level - 4000 Hz##OTHER## | COBIE Octave sound power level - 8000 Hz##OTHER## | COBIE Water content of heating coil##OTHER## | COBIE Weight##OTHER##
MH-6-A | 50°C | 60°C | 90°C | 800 kPa | 3x400 V AC | +/-5% | 50 Hz | 1.5 kW | 2.9A | 13A | IP 54 | 6000.0 | 537.0 | 48.5% | 0.90 kW | 33.1/33.8 kW | 14.4/14.7 m | 33.9/33.2 °C | 7/8 kPa | 1424/1451 l/h | 19.1/19.7 kW | 18.8/19.5 m | 27.0/26.3 °C | 2/3 kPa | 820/848 l/h | 58 dB(A) | 80 dB(A) | 57 dB | 61 dB | 67 dB | 72 dB | 76 dB | 73 dB | 67 dB | 59 dB | 900.0 | 758.0 | 1077.0 | 999.0 | 760.0 | 420.0 | 850.0 | 1089.0 | 1660.0 | 31.75 | 4.6 l | 165 kg | 50°C | 60°C | 90°C | 800 kPa | 3x400 V AC | +/-5% | 50 Hz | 1.5 kW | 2.9A | 13A | IP 54 | 6000.0 | 537.0 | 48.5% | 0.90 kW | 33.1/33.8 kW | 14.4/14.7 m | 33.9/33.2 °C | 7/8 kPa | 1424/1451 l/h | 19.1/19.7 kW | 18.8/19.5 m | 27.0/26.3 °C | 2/3 kPa | 820/848 l/h | 58 dB(A) | 80 dB(A) | 57 dB | 61 dB | 67 dB | 72 dB | 76 dB | 73 dB | 67 dB | 59 dB | 4.6 l | 165 kg
MH-6-B | 50°C | 60°C | 90°C | 800 kPa | 3x400 V AC | +/-5% | 50 Hz | 1.5 kW | 2.9A | 13A | IP 54 | 6000.0 | 537.0 | 48.5% | 1.05 kW | 47.5/48.4 kW | 12.1/12.2 m | 41.0/40.5 °C | 13/14 kPa | 2040/2079 l/h | 27.4/28.3 kW | 15.7/16.1 m | 31.1/30.5 °C | 4/5 kPa | 1177/1216 l/h | 58 dB(A) | 80 dB(A) | 57 dB | 61 dB | 67 dB | 72 dB | 76 dB | 73 dB | 67 dB | 59 dB | 900.0 | 758.0 | 1077.0 | 999.0 | 760.0 | 420.0 | 850.0 | 1089.0 | 1660.0 | 31.75 | 4.6 l | 165 kg | 50°C | 60°C | 90°C | 800 kPa | 3x400 V AC | +/-5% | 50 Hz | 1.5 kW | 2.9A | 13A | IP 54 | 6000.0 | 537.0 | 48.5% | 1.05 kW | 47.5/48.4 kW | 12.1/12.2 m | 41.0/40.5 °C | 13/14 kPa | 2040/2079 l/h | 27.4/28.3 kW | 15.7/16.1 m | 31.1/30.5 °C | 4/5 kPa | 1177/1216 l/h | 58 dB(A) | 80 dB(A) | 57 dB | 61 dB | 67 dB | 72 dB | 76 dB | 73 dB | 67 dB | 59 dB | 4.6 l | 165 kg
MH-6-C | 50°C | 60°C | 90°C | 800 kPa | 3x400 V AC | +/-5% | 50 Hz | 1.5 kW | 2.9A | 13A | IP 54 | 6000.0 | 537.0 | 48.5% | 1.29 kW | 76.8/78.2 kW | 9.7/9.7 m | 55.5/55.2 °C | 18/19 kPa | 3297/3358 l/h | 45.7/47.2 kW | 12.3/12.4 m | 40.1/39.9 °C | 7/7 kPa | 1965/2026 l/h | 58 dB(A) | 80 dB(A) | 57 dB | 61 dB | 67 dB | 72 dB | 76 dB | 73 dB | 67 dB | 59 dB | 900.0 | 758.0 | 1077.0 | 999.0 | 760.0 | 420.0 | 850.0 | 1089.0 | 1660.0 | 31.75 | 7.9 l | 172 kg | 50°C | 60°C | 90°C | 800 kPa | 3x400 V AC | +/-5% | 50 Hz | 1.5 kW | 2.9A | 13A | IP 54 | 6000.0 | 537.0 | 48.5% | 1.29 kW | 76.8/78.2 kW | 9.7/9.7 m | 55.5/55.2 °C | 18/19 kPa | 3297/3358 l/h | 45.7/47.2 kW | 12.3/12.4 m | 40.1/39.9 °C | 7/7 kPa | 1965/2026 l/h | 58 dB(A) | 80 dB(A) | 57 dB | 61 dB | 67 dB | 72 dB | 76 dB | 73 dB | 67 dB | 59 dB | 7.9 l | 172 kg
MH-9-A | 50°C | 60°C | 90°C | 800 kPa | 3x400 V AC | +/-5% | 50 Hz | 2.1 kW | 4.0A | 13A | IP 54 | 9000.0 | 946.0 | 43.0% | 1.37 kW | 56.1/57.1 kW | 14.4/14.6 m | 36.0/35.4 °C | 8/8 kPa | 2409/2455 l/h | 32.3/33.4 kW | 18.8/19.4 m | 28.2/27.5 °C | 3/3 kPa | 1387/1433 l/h | 60 dB(A) | 82 dB(A) | 62 dB | 66 dB | 71 dB | 74 dB | 77 dB | 76 dB | 71 dB | 64 dB | 1100.0 | 882.0 | 1127.0 | 1049.0 | 935.0 | 500.0 | 1050.0 | 1289.0 | 1810.0 | 38.10 | 7.4 l | 217 kg | 50°C | 60°C | 90°C | 800 kPa | 3x400 V AC | +/-5% | 50 Hz | 2.1 kW | 4.0A | 13A | IP 54 | 9000.0 | 946.0 | 43.0% | 1.37 kW | 56.1/57.1 kW | 14.4/14.6 m | 36.0/35.4 °C | 8/8 kPa | 2409/2455 l/h | 32.3/33.4 kW | 18.8/19.4 m | 28.2/27.5 °C | 3/3 kPa | 1387/1433 l/h | 60 dB(A) | 82 dB(A) | 62 dB | 66 dB | 71 dB | 74 dB | 77 dB | 76 dB | 71 dB | 64 dB | 7.4 l | 217 kg
MH-9-B | 50°C | 60°C | 90°C | 800 kPa | 3x400 V AC | +/-5% | 50 Hz | 2.1 kW | 4.0A | 13A | IP 54 | 9000.0 | 946.0 | 43.0% | 1.49 kW | 71.9/73.3 kW | 12.8/12.9 m | 41.2/40.7 °C | 12/13 kPa | 3090/3149 l/h | 41.3/42.7 kW | 16.7/17.0 m | 31.1/30.6 °C | 4/4 kPa | 1775/1834 l/h | 60 dB(A) | 82 dB(A) | 62 dB | 66 dB | 71 dB | 74 dB | 77 dB | 76 dB | 71 dB | 64 dB | 1100.0 | 882.0 | 1127.0 | 1049.0 | 935.0 | 500.0 | 1050.0 | 1289.0 | 1810.0 | 38.10 | 7.4 l | 217 kg | 50°C | 60°C | 90°C | 800 kPa | 3x400 V AC | +/-5% | 50 Hz | 2.1 kW | 4.0A | 13A | IP 54 | 9000.0 | 946.0 | 43.0% | 1.49 kW | 71.9/73.3 kW | 12.8/12.9 m | 41.2/40.7 °C | 12/13 kPa | 3090/3149 l/h | 41.3/42.7 kW | 16.7/17.0 m | 31.1/30.6 °C | 4/4 kPa | 1775/1834 l/h | 60 dB(A) | 82 dB(A) | 62 dB | 66 dB | 71 dB | 74 dB | 77 dB | 76 dB | 71 dB | 64 dB | 7.4 l | 217 kg
MH-9-C | 50°C | 60°C | 90°C | 800 kPa | 3x400 V AC | +/-5% | 50 Hz | 2.1 kW | 4.0A | 13A | IP 54 | 9000.0 | 946.0 | 43.0% | 1.91 kW | 119.0/121.2 kW | 10.1/10.1 m | 56.8/56.5 °C | 18/19 kPa | 5113/5208 l/h | 71.0/73.2 kW | 12.9/12.9 m | 40.9/40.7 °C | 7/7 kPa | 3050/3145 l/h | 60 dB(A) | 82 dB(A) | 62 dB | 66 dB | 71 dB | 74 dB | 77 dB | 76 dB | 71 dB | 64 dB | 1100.0 | 882.0 | 1127.0 | 1049.0 | 935.0 | 500.0 | 1050.0 | 1289.0 | 1810.0 | 38.10 | 12.4 l | 228 kg | 50°C | 60°C | 90°C | 800 kPa | 3x400 V AC | +/-5% | 50 Hz | 2.1 kW | 4.0A | 13A | IP 54 | 9000.0 | 946.0 | 43.0% | 1.91 kW | 119.0/121.2 kW | 10.1/10.1 m | 56.8/56.5 °C | 18/19 kPa | 5113/5208 l/h | 71.0/73.2 kW | 12.9/12.9 m | 40.9/40.7 °C | 7/7 kPa | 3050/3145 l/h | 60 dB(A) | 82 dB(A) | 62 dB | 66 dB | 71 dB | 74 dB | 77 dB | 76 dB | 71 dB | 64 dB | 12.4 l | 228 kg