## List1
| Extract air temperature max.##OTHER## | Supply air temperature max.##OTHER## | Temperature of the heating medium max.##OTHER## | Pressure of the heating medium max.##OTHER## | Air flow rate##OTHER## | Condensate quantity##OTHER## | Supply voltage##OTHER## | Permitted voltage tolerance##OTHER## | Frequency##OTHER## | Connected load##OTHER## | Current consumption max.##OTHER## | Series fuse##OTHER## | Protection rating##OTHER## | Nominal air flow rate##HVAC_AIR_FLOW##CUBIC_METERS_PER_HOUR | Floor area covered##AREA##SQUARE_METERS | Static efficiency of the fans##OTHER## | Effective electric power input##OTHER## | Heat output -5/-15 °C (80/60 °C)##OTHER## | Maximum mounting height -5/-15 °C (80/60 °C)##OTHER## | Supply air temperature -5/-15 °C (80/60 °C)##OTHER## | Water pressure drop -5/-15 °C (80/60 °C)##OTHER## | Water quantity -5/-15 °C (80/60 °C)##OTHER## | Heat output -5/-15 °C (60/40 °C)##OTHER## | Maximum mounting height -5/-15 °C (60/40 °C)##OTHER## | Supply air temperature -5/-15 °C (60/40 °C)##OTHER## | Water pressure drop -5/-15 °C (60/40 °C)##OTHER## | Water quantity -5/-15 °C (60/40 °C)##OTHER## | Sensible cooling capacity 28 °C (40/60 %) - 6/12 °C##OTHER## | Sensible cooling capacity 32 °C (40/60 %) - 6/12 °C##OTHER## | Total cooling capacity 28 °C (40/60 %) - 6/12 °C##OTHER## | Total cooling capacity 32 °C (40/60 %) - 6/12 °C##OTHER## | Supply air temperature 28 °C (40/60 %) - 6/12 °C##OTHER## | Supply air temperature 32 °C (40/60 %) - 6/12 °C##OTHER## | Water pressure drop 28 °C (40/60 %) - 6/12 °C##OTHER## | Water pressure drop 32 °C (40/60 %) - 6/12 °C##OTHER## | Water quantity 28 °C (40/60 %) - 6/12 °C##OTHER## | Water quantity 32 °C (40/60 %) - 6/12 °C##OTHER## | Condensate quantity 28 °C (40/60 %) - 6/12 °C##OTHER## | Condensate quantity 32 °C (40/60 %) - 6/12 °C##OTHER## | Sensible cooling capacity 28 °C (40/60 %) - 8/14 °C##OTHER## | Sensible cooling capacity 32 °C (40/60 %) - 8/14 °C##OTHER## | Total cooling capacity 28 °C (40/60 %) - 8/14 °C##OTHER## | Total cooling capacity 32 °C (40/60 %) - 8/14 °C##OTHER## | Supply air temperature 28 °C (40/60 %) - 8/14 °C##OTHER## | Supply air temperature 32 °C (40/60 %) - 8/14 °C##OTHER## | Water pressure drop 28 °C (40/60 %) - 8/14 °C##OTHER## | Water pressure drop 32 °C (40/60 %) - 8/14 °C##OTHER## | Water quantity 28 °C (40/60 %) - 8/14 °C##OTHER## | Water quantity 32 °C (40/60 %) - 8/14 °C##OTHER## | Condensate quantity 28 °C (40/60 %) - 8/14 °C##OTHER## | Condensate quantity 32 °C (40/60 %) - 8/14 °C##OTHER## | Sound pressure level (at a distance of 5 m)##OTHER## | Total sound power level##OTHER## | Octave sound power level - 63 Hz##OTHER## | Octave sound power level - 125 Hz##OTHER## | Octave sound power level - 250 Hz##OTHER## | Octave sound power level - 500 Hz##OTHER## | Octave sound power level - 1000 Hz##OTHER## | Octave sound power level - 2000 Hz##OTHER## | Octave sound power level - 4000 Hz##OTHER## | Octave sound power level - 8000 Hz##OTHER## | (X)##LENGTH##MILLIMETERS | A##LENGTH##MILLIMETERS | F##LENGTH##MILLIMETERS | G##LENGTH##MILLIMETERS | H##LENGTH##MILLIMETERS | I##LENGTH##MILLIMETERS | J##LENGTH##MILLIMETERS | K##LENGTH##MILLIMETERS | L##LENGTH##MILLIMETERS | N##LENGTH##MILLIMETERS | O##LENGTH##MILLIMETERS | P##LENGTH##MILLIMETERS | R##LENGTH##MILLIMETERS | T##LENGTH##MILLIMETERS | U##LENGTH##MILLIMETERS | V##LENGTH##MILLIMETERS | W##LENGTH##MILLIMETERS | M##LENGTH##MILLIMETERS | Water content of heating coil##OTHER## | Water content of cooling coil##OTHER## | Weight##OTHER## | COBIE Extract air temperature max.##OTHER## | COBIE Supply air temperature max.##OTHER## | COBIE Temperature of the heating medium max.##OTHER## | COBIE Pressure of the heating medium max.##OTHER## | COBIE Air flow rate##OTHER## | COBIE Condensate quantity##OTHER## | COBIE Supply voltage##OTHER## | COBIE Permitted voltage tolerance##OTHER## | COBIE Frequency##OTHER## | COBIE Connected load##OTHER## | COBIE Current consumption max.##OTHER## | COBIE Series fuse##OTHER## | COBIE Protection rating##OTHER## | COBIE Nominal air flow rate##HVAC_AIR_FLOW##CUBIC_METERS_PER_HOUR | COBIE Floor area covered##AREA##SQUARE_METERS | COBIE Static efficiency of the fans##OTHER## | COBIE Effective electric power input##OTHER## | COBIE Heat output -5/-15 °C (80/60 °C)##OTHER## | COBIE Maximum mounting height -5/-15 °C (80/60 °C)##OTHER## | COBIE Supply air temperature -5/-15 °C (80/60 °C)##OTHER## | COBIE Water pressure drop -5/-15 °C (80/60 °C)##OTHER## | COBIE Water quantity -5/-15 °C (80/60 °C)##OTHER## | COBIE Heat output -5/-15 °C (60/40 °C)##OTHER## | COBIE Maximum mounting height -5/-15 °C (60/40 °C)##OTHER## | COBIE Supply air temperature -5/-15 °C (60/40 °C)##OTHER## | COBIE Water pressure drop -5/-15 °C (60/40 °C)##OTHER## | COBIE Water quantity -5/-15 °C (60/40 °C)##OTHER## | COBIE Sensible cooling capacity 28 °C (40/60 %) - 6/12 °C##OTHER## | COBIE Sensible cooling capacity 32 °C (40/60 %) - 6/12 °C##OTHER## | COBIE Total cooling capacity 28 °C (40/60 %) - 6/12 °C##OTHER## | COBIE Total cooling capacity 32 °C (40/60 %) - 6/12 °C##OTHER## | COBIE Supply air temperature 28 °C (40/60 %) - 6/12 °C##OTHER## | COBIE Supply air temperature 32 °C (40/60 %) - 6/12 °C##OTHER## | COBIE Water pressure drop 28 °C (40/60 %) - 6/12 °C##OTHER## | COBIE Water pressure drop 32 °C (40/60 %) - 6/12 °C##OTHER## | COBIE Water quantity 28 °C (40/60 %) - 6/12 °C##OTHER## | COBIE Water quantity 32 °C (40/60 %) - 6/12 °C##OTHER## | COBIE Condensate quantity 28 °C (40/60 %) - 6/12 °C##OTHER## | COBIE Condensate quantity 32 °C (40/60 %) - 6/12 °C##OTHER## | COBIE Sensible cooling capacity 28 °C (40/60 %) - 8/14 °C##OTHER## | COBIE Sensible cooling capacity 32 °C (40/60 %) - 8/14 °C##OTHER## | COBIE Total cooling capacity 28 °C (40/60 %) - 8/14 °C##OTHER## | COBIE Total cooling capacity 32 °C (40/60 %) - 8/14 °C##OTHER## | COBIE Supply air temperature 28 °C (40/60 %) - 8/14 °C##OTHER## | COBIE Supply air temperature 32 °C (40/60 %) - 8/14 °C##OTHER## | COBIE Water pressure drop 28 °C (40/60 %) - 8/14 °C##OTHER## | COBIE Water pressure drop 32 °C (40/60 %) - 8/14 °C##OTHER## | COBIE Water quantity 28 °C (40/60 %) - 8/14 °C##OTHER## | COBIE Water quantity 32 °C (40/60 %) - 8/14 °C##OTHER## | COBIE Condensate quantity 28 °C (40/60 %) - 8/14 °C##OTHER## | COBIE Condensate quantity 32 °C (40/60 %) - 8/14 °C##OTHER## | COBIE Sound pressure level (at a distance of 5 m)##OTHER## | COBIE Total sound power level##OTHER## | COBIE Octave sound power level - 63 Hz##OTHER## | COBIE Octave sound power level - 125 Hz##OTHER## | COBIE Octave sound power level - 250 Hz##OTHER## | COBIE Octave sound power level - 500 Hz##OTHER## | COBIE Octave sound power level - 1000 Hz##OTHER## | COBIE Octave sound power level - 2000 Hz##OTHER## | COBIE Octave sound power level - 4000 Hz##OTHER## | COBIE Octave sound power level - 8000 Hz##OTHER## | COBIE Water content of heating coil##OTHER## | COBIE Water content of cooling coil##OTHER## | COBIE Weight##OTHER##
MHC-6-AC | 50°C | 60°C | 90°C | 800 kPa | 3100 m3/h | 90 kg/h | 3x400 V AC | +/-5% | 50 Hz | 3.6 kW | 5.9A | 13A | IP 54 | 6000.0 | 537.0 | 63.6% | 0.92 kW | 33.1/33.8 kW | 14.4/14.7 m | 33.9/33.2 °C | 7/8 kPa | 1424/1451 l/h | 19.1/13.7 kW | 18.8/19.5 m | 27.0/26.3 °C | 2/3 kPa | 820/848 l/h | 21.0/20.7 kW | 25.7/25.4 kW | 21.0/20.7 kW | 32.3/34.1 kW | 14.0/14.2 °C | 15.7/15.8 °C | 16/16 kPa | 39/43 kPa | 3000/2961 l/h | 4630/4884 l/h | 0.0/0.0 kg/h | 4.1/7.1 kg/h | 18.5/18.2 kW | 23.3/23.0 kW | 18.5/18.2 kW | 26.1/27.8 kW | 15.2/15.4 °C | 16.9/17.0 °C | 13/12 kPa | 25/29 kPa | 2649/2609 l/h | 3734/3988 l/h | 0.0/0.0 kg/h | 4.1/7.1 kg/h | 56 dB(A) | 77 dB(A) | 43 dB | 61 dB | 64 dB | 69 dB | 73 dB | 72 dB | 69 dB | 60 dB | 1120.0 | 900.0 | 758.0 | 936.0 | 858.0 | 760.0 | 31.75 | 1550.0 | 594.0 | 31.75 | 420.0 | 850.0 | 2374.0 | 1069.0 | 1020.0 | 1184.0 | 1106.0 | 25.40 | 4.6 l | 7.9 l | 295 kg | 50°C | 60°C | 90°C | 800 kPa | 3100 m3/h | 90 kg/h | 3x400 V AC | +/-5% | 50 Hz | 3.6 kW | 5.9A | 13A | IP 54 | 6000.0 | 537.0 | 63.6% | 0.72 kW | 32.8/30.3 kW | 13.4/14.0 m | 34.2/37.0 °C | 7/6 kPa | 1410/1301 l/h | 18.8/16.2 kW | 16.8/17.9 m | 27.3/30.0 °C | 2/2 kPa | 807/697 l/h | 20.4/18.5 kW | 25.2/23.2 kW | 20.4/27.7 kW | 31.1/43.7 kW | 13.9/14.9 °C | 15.5/16.5 °C | 15/28 kPa | 36/71 kPa | 2925/3960 l/h | 4448/6263 l/h | 0.0/13.5 kg/h | 8.6/30.2 kg/h | 20.4/16.0 kW | 22.7/20.8 kW | 20.4/21.4 kW | 24.8/37.5 kW | 13.9/16.1 °C | 16.7/17.7 °C | 15/17 kPa | 23/52 kPa | 2925/3064 l/h | 3552/5367 l/h | 0.0/7.9 kg/h | 3.0/24.6 kg/h | 54 dB(A) | 76 dB(A) | 41 dB | 59 dB | 62 dB | 68 dB | 71 dB | 71 dB | 67 dB | 58 dB | 4.6 l | 7.9 l | 248 kg
MHC-6-BC | 50°C | 60°C | 90°C | 800 kPa | 3100 m3/h | 90 kg/h | 3x400 V AC | +/-5% | 50 Hz | 3.6 kW | 5.9A | 13A | IP 54 | 6000.0 | 537.0 | 63.6% | 0.97 kW | 47.5/48.4 kW | 12.1/12.2 m | 41.0/40.5 °C | 13/14 kPa | 2040/2079 l/h | 27.4/28.3 kW | 15.7/16.1 m | 31.1/30.5 °C | 4/5 kPa | 1177/1216 l/h | 21.0/20.7 kW | 25.7/25.4 kW | 21.0/20.7 kW | 32.3/34.1 kW | 14.0/14.2 °C | 15.7/15.8 °C | 16/16 kPa | 39/43 kPa | 3000/2961 l/h | 4630/4884 l/h | 0.0/0.0 kg/h | 4.1/7.1 kg/h | 18.5/18.2 kW | 23.3/23.0 kW | 18.5/18.2 kW | 26.1/27.8 kW | 15.2/15.4 °C | 16.9/17.0 °C | 13/12 kPa | 25/29 kPa | 2649/2609 l/h | 3734/3988 l/h | 0.0/0.0 kg/h | 4.1/7.1 kg/h | 56 dB(A) | 77 dB(A) | 43 dB | 61 dB | 64 dB | 69 dB | 73 dB | 72 dB | 69 dB | 60 dB | 1120.0 | 900.0 | 758.0 | 936.0 | 858.0 | 760.0 | 31.75 | 1550.0 | 594.0 | 31.75 | 420.0 | 850.0 | 2374.0 | 1069.0 | 1020.0 | 1184.0 | 1106.0 | 25.40 | 4.6 l | 7.9 l | 299 kg | 50°C | 60°C | 90°C | 800 kPa | 3100 m3/h | 90 kg/h | 3x400 V AC | +/-5% | 50 Hz | 3.6 kW | 5.9A | 13A | IP 54 | 6000.0 | 537.0 | 63.6% | 0.76 kW | 47.0/43.4 kW | 11.6/12.0 m | 41.3/43.5 °C | 13/11 kPa | 2020/1864 l/h | 26.9/23.3 kW | 14.6/15.5 m | 31.3/33.5 °C | 4/3 kPa | 1157/1001 l/h | 20.4/18.5 kW | 25.2/23.2 kW | 20.4/27.7 kW | 31.1/43.7 kW | 13.9/14.9 °C | 15.5/16.5 °C | 15/28 kPa | 36/71 kPa | 2925/3960 l/h | 4448/6263 l/h | 0.0/13.5 kg/h | 8.6/30.2 kg/h | 20.4/16.0 kW | 22.7/20.8 kW | 20.4/21.4 kW | 24.8/37.5 kW | 13.9/16.1 °C | 16.7/17.7 °C | 15/17 kPa | 23/52 kPa | 2925/3064 l/h | 3552/5367 l/h | 0.0/7.9 kg/h | 3.0/24.6 kg/h | 54 dB(A) | 76 dB(A) | 41 dB | 59 dB | 62 dB | 68 dB | 71 dB | 71 dB | 67 dB | 58 dB | 4.6 l | 7.9 l | 248 kg
MHC-6-CC | 50°C | 60°C | 90°C | 800 kPa | 3100 m3/h | 90 kg/h | 3x400 V AC | +/-5% | 50 Hz | 3.6 kW | 5.9A | 13A | IP 54 | 6000.0 | 537.0 | 63.6% | 1.09 kW | 76.8/78.2 kW | 9.7/9.7 m | 55.5/55.2 °C | 18/19 kPa | 3297/3358 l/h | 45.7/47.2 kW | 12.3/12.4 m | 40.1/39.9 °C | 7/7 kPa | 1965/2026 l/h | 21.0/20.7 kW | 25.7/25.4 kW | 21.0/20.7 kW | 32.3/34.1 kW | 14.0/14.2 °C | 15.7/15.8 °C | 16/16 kPa | 39/43 kPa | 3000/2961 l/h | 4630/4884 l/h | 0.0/0.0 kg/h | 4.1/7.1 kg/h | 18.5/18.2 kW | 23.3/23.0 kW | 18.5/18.2 kW | 26.1/27.8 kW | 15.2/15.4 °C | 16.9/17.0 °C | 13/12 kPa | 25/29 kPa | 2649/2609 l/h | 3734/3988 l/h | 0.0/0.0 kg/h | 4.1/7.1 kg/h | 56 dB(A) | 77 dB(A) | 43 dB | 61 dB | 64 dB | 69 dB | 73 dB | 72 dB | 69 dB | 60 dB | 1120.0 | 900.0 | 758.0 | 936.0 | 858.0 | 760.0 | 31.75 | 1550.0 | 594.0 | 31.75 | 420.0 | 850.0 | 2374.0 | 1069.0 | 1020.0 | 1184.0 | 1106.0 | 25.40 | 7.9 l | 7.9 l | 305 kg | 50°C | 60°C | 90°C | 800 kPa | 3100 m3/h | 90 kg/h | 3x400 V AC | +/-5% | 50 Hz | 3.6 kW | 5.9A | 13A | IP 54 | 6000.0 | 537.0 | 63.6% | 0.87 kW | 76.0/70.3 kW | 9.4/9.8 m | 55.6/56.8 °C | 18/16 kPa | 3267/3022 l/h | 45.0/39.3 kW | 11.8/12.5 m | 40.3/41.5 °C | 6/5 kPa | 1935/1690 l/h | 20.4/18.5 kW | 25.2/23.2 kW | 20.4/27.7 kW | 31.1/43.7 kW | 13.9/14.9 °C | 15.5/16.5 °C | 15/28 kPa | 36/71 kPa | 2925/3960 l/h | 4448/6263 l/h | 0.0/13.5 kg/h | 8.6/30.2 kg/h | 20.4/16.0 kW | 22.7/20.8 kW | 20.4/21.4 kW | 24.8/37.5 kW | 13.9/16.1 °C | 16.7/17.7 °C | 15/17 kPa | 23/52 kPa | 2925/3064 l/h | 3552/5367 l/h | 0.0/7.9 kg/h | 3.0/24.6 kg/h | 54 dB(A) | 76 dB(A) | 41 dB | 59 dB | 62 dB | 68 dB | 71 dB | 71 dB | 67 dB | 58 dB | 7.9 l | 7.9 l | 255 kg
MHC-9-AC | 50°C | 60°C | 90°C | 800 kPa | 5000 m3/h | 150 kg/h | 3x400 V AC | +/-5% | 50 Hz | 3.6 kW | 5.9A | 13A | IP 54 | 9000.0 | 946.0 | 63.6% | 1.59kW | 56.1/57.1 kW | 14.4/14.6 m | 36.0/35.4 °C | 8/8 kPa | 2409/2455 l/h | 32.3/33.4 kW | 18.8/19.4 m | 28.2/27.5 °C | 3/3 kPa | 1387/1433 l/h | 32.2/31.8 kW | 39.7/39.3 kW | 32.2/31.8 kW | 51.9/54.7 kW | 13.8/13.9 °C | 15.3/15.4 °C | 16/16 kPa | 41/46 kPa | 4614/4554 l/h | 7432/7829 l/h | 0.0/0.0 kg/h | 0.0/4.0 kg/h | 28.4/28.0 kW | 35.8/35.4 kW | 28.4/28.0 kW | 35.8/38.1 kW | 15.0/15.2 °C | 16.6/16.7 °C | 12/12 kPa | 20/22 kPa | 4064/4004 l/h | 5131/5459 l/h | 0.0/0.0 kg/h | 0.0/4.0 kg/h | 60 dB(A) | 82 dB(A) | 47 dB | 67 dB | 70 dB | 74 dB | 78 dB | 76 dB | 74 dB | 67 dB | 1242.0 | 1100.0 | 882.0 | 951.0 | 873.0 | 935.0 | 38.10 | 1622.0 | 846.0 | 38.10 | 500.0 | 1050.0 | 2496.0 | 1104.0 | 1220.0 | 1235.0 | 1157.0 | 25.40 | 7.4 l | 12.4 l | 377 kg | 50°C | 60°C | 90°C | 800 kPa | 5000 m3/h | 150 kg/h | 3x400 V AC | +/-5% | 50 Hz | 3.6 kW | 5.9A | 13A | IP 54 | 9000.0 | 946.0 | 63.6% | 1.37 kW | 55.5/51.2 kW | 13.6/14.1 m | 36.3/38.9 °C | 8/7 kPa | 2386/2201 l/h | 31.7/27.4 kW | 17.0/18.1 m | 28.5/31.1 °C | 3/2 kPa | 1364/1179 l/h | 31.4/28.4 kW | 38.8/35.9 kW | 31.4/44.7 kW | 49.9/69.8 kW | 13.6/14.6 °C | 15.2/16.2 °C | 15/31 kPa | 38/75 kPa | 4496/6401 l/h | 7149/9989 l/h | 0.0/23.9 kg/h | 16.3/49.8 kg/h | 31.4/24.6 kW | 35.0/32.0 kW | 31.4/28.2 kW | 35.0/53.2 kW | 13.6/15.9 °C | 16.4/17.4 °C | 15/12 kPa | 19/44 kPa | 4496/4031 l/h | 5013/7619 l/h | 0.0/5.2 kg/h | 0.0/31.1 kg/h | 60 dB(A) | 82 dB(A) | 47 dB | 66 dB | 69 dB | 74 dB | 77 dB | 76 dB | 74 dB | 67 dB | 7.4 l | 12.4 l | 318 kg
MHC-9-BC | 50°C | 60°C | 90°C | 800 kPa | 5000 m3/h | 150 kg/h | 3x400 V AC | +/-5% | 50 Hz | 3.6 kW | 5.9A | 13A | IP 54 | 9000.0 | 946.0 | 63.6% | 1.72 kW | 71.9/73.3 kW | 12.8/12.9 m | 41.2/40.7 °C | 12/13 kPa | 3090/3149 l/h | 41.3/42.7 kW | 16.7/17.0 m | 31.1/30.6 °C | 4/4 kPa | 1775/1834 l/h | 32.2/31.8 kW | 39.7/39.3 kW | 32.2/31.8 kW | 51.9/54.7 kW | 13.8/13.9 °C | 15.3/15.4 °C | 16/16 kPa | 41/46 kPa | 4614/4554 l/h | 7432/7829 l/h | 0.0/0.0 kg/h | 0.0/4.0 kg/h | 28.4/28.0 kW | 35.8/35.4 kW | 28.4/28.0 kW | 35.8/38.1 kW | 15.0/15.2 °C | 16.6/16.7 °C | 12/12 kPa | 20/22 kPa | 4064/4004 l/h | 5131/5459 l/h | 0.0/0.0 kg/h | 0.0/4.0 kg/h | 60 dB(A) | 82 dB(A) | 47 dB | 67 dB | 70 dB | 74 dB | 78 dB | 76 dB | 74 dB | 67 dB | 1242.0 | 1100.0 | 882.0 | 951.0 | 873.0 | 935.0 | 38.10 | 1622.0 | 846.0 | 38.10 | 500.0 | 1050.0 | 2496.0 | 1104.0 | 1220.0 | 1235.0 | 1157.0 | 25.40 | 7.4 l | 12.4 l | 377 kg | 50°C | 60°C | 90°C | 800 kPa | 5000 m3/h | 150 kg/h | 3x400 V AC | +/-5% | 50 Hz | 3.6 kW | 5.9A | 13A | IP 54 | 9000.0 | 946.0 | 63.6% | 1.49 kW | 71.2/65.7 kW | 12.2/12.7 m | 41.5/43.7 °C | 12/10 kPa | 3060/2823 l/h | 40.6/35.1 kW | 15.4/16.5 m | 31.4/33.6 °C | 4/3 kPa | 1746/1509 l/h | 31.4/28.4 kW | 38.8/35.9 kW | 31.4/44.7 kW | 49.9/69.8 kW | 13.6/14.6 °C | 15.2/16.2 °C | 15/31 kPa | 38/75 kPa | 4496/6401 l/h | 7149/9989 l/h | 0.0/23.9 kg/h | 16.3/49.8 kg/h | 31.4/24.6 kW | 35.0/32.0 kW | 31.4/28.2 kW | 35.0/53.2 kW | 13.6/15.9 °C | 16.4/17.4 °C | 15/12 kPa | 19/44 kPa | 4496/4031 l/h | 5013/7619 l/h | 0.0/5.2 kg/h | 0.0/31.1 kg/h | 60 dB(A) | 82 dB(A) | 47 dB | 66 dB | 69 dB | 74 dB | 77 dB | 76 dB | 74 dB | 67 dB | 7.4 l | 12.4 l | 318 kg
MHC-9-CC | 50°C | 60°C | 90°C | 800 kPa | 5000 m3/h | 150 kg/h | 3x400 V AC | +/-5% | 50 Hz | 3.6 kW | 5.9A | 13A | IP 54 | 9000.0 | 946.0 | 63.6% | 1.64 kW | 119.0/121.2 kW | 10.1/10.1 m | 56.8/56.5 °C | 18/19 kPa | 5113/5208 l/h | 71.0/73.2 kW | 12.9/12.9 m | 40.9/40.7 °C | 7/7 kPa | 3050/3145 l/h | 32.2/31.8 kW | 39.7/39.3 kW | 32.2/31.8 kW | 51.9/54.7 kW | 13.8/13.9°C | 15.3/15.4 °C | 16/16 kPa | 41/46 kPa | 4614/4554 l/h | 7432/7829 l/h | 0.0/0.0 kg/h | 0.0/4.0 kg/h | 28.4/28.0 kW | 35.8/35.4 kW | 28.4/28.0 kW | 35.8/38.1 kW | 15.0/15.2 °C | 16.6/16.7 °C | 12/12 kPa | 20/22 kPa | 4064/4004 l/h | 5131/5459 l/h | 0.0/0.0 kg/h | 0.0/4.0 kg/h | 60 dB(A) | 82 dB(A) | 47 dB | 67 dB | 70 dB | 74 dB | 78 dB | 76 dB | 74 dB | 67 dB | 1242.0 | 1100.0 | 882.0 | 951.0 | 873.0 | 935.0 | 38.10 | 1622.0 | 846.0 | 38.10 | 500.0 | 1050.0 | 2496.0 | 1104.0 | 1220.0 | 1235.0 | 1157.0 | 25.40 | 12.4 l | 12.4 l | 388 kg | 50°C | 60°C | 90°C | 800 kPa | 5000 m3/h | 150 kg/h | 3x400 V AC | +/-5% | 50 Hz | 3.6 kW | 5.9A | 13A | IP 54 | 9000.0 | 946.0 | 63.6% | 1.42 kW | 117.9/109.1 kW | 9.8/10.2 m | 56.9/58.0 °C | 18/15 kPa | 5066/4686 l/h | 69.9/61.0 kW | 12.3/13.1 m | 41.1/42.1 °C | 6/5 kPa | 3003/2622 l/h | 31.4/28.4 kW | 38.8/35.9 kW | 31.4/44.7 kW | 49.9/69.8 kW | 13.6/14.6 °C | 15.2/16.2 °C | 15/31 kPa | 38/75 kPa | 4496/6401 l/h | 7149/9989 l/h | 0.0/23.9 kg/h | 16.3/49.8 kg/h | 31.4/24.6 kW | 35.0/32.0 kW | 31.4/28.2 kW | 35.0/53.2 kW | 13.6/15.9 °C | 16.4/17.4 °C | 15/12 kPa | 19/44 kPa | 4496/4031 l/h | 5013/7619 l/h | 0.0/5.2 kg/h | 0.0/31.1 kg/h | 60 dB(A) | 82 dB(A) | 47 dB | 66 dB | 69 dB | 74 dB | 77 dB | 76 dB | 74 dB | 67 dB | 12.4 l | 12.4 l | 329 kg
MHC-9-AD | 50°C | 60°C | 90°C | 800 kPa | 5000 m3/h | 150 kg/h | 3x400 V AC | +/-5% | 50 Hz | 3.6 kW | 5.9A | 13A | IP 54 | 9000.0 | 946.0 | 63.6% | 1.77 kW | 56.1/57.1 kW | 14.4/14.6 m | 36.0/35.4 °C | 8/8 kPa | 2409/2455 l/h | 32.3/33.4 kW | 18.8/19.4 m | 28.2/27.5 °C | 3/3 kPa | 1387/1433 l/h | 38.1/37.7 kW | 47.4/47.1 kW | 38.1/37.8 kW | 64.8/68.3 kW | 11.8/12.0 °C | 12.7/12.9 °C | 13/13 kPa | 39/43 kPa | 5451/5409 l/h | 9285/9785 l/h | 0.0/0.0 kg/h | 15.7/21.3 kg/h | 33.2/32.9 kW | 42.6/42.2 kW | 33.2/32.9 kW | 53.3/56.7 kW | 13.4/13.6 °C | 14.3/14.5 °C | 10/10 kPa | 26/30 kPa | 4756/4706 l/h | 7626/8126 l/h | 0.0/0.0 kg/h | 15.7/21.3 kg/h | 60 dB(A) | 82 dB(A) | 47 dB | 67 dB | 70 dB | 74 dB | 78 dB | 76 dB | 74 dB | 67 dB | 1242.0 | 1100.0 | 882.0 | 951.0 | 873.0 | 935.0 | 50.80 | 1622.0 | 846.0 | 38.10 | 500.0 | 1050.0 | 2496.0 | 1104.0 | 1220.0 | 1244.0 | 1149.0 | 25.40 | 7.4 l | 19.2 l | 388 kg | 50°C | 60°C | 90°C | 800 kPa | 5000 m3/h | 150 kg/h | 3x400 V AC | +/-5% | 50 Hz | 3.6 kW | 5.9A | 13A | IP 54 | 9000.0 | 946.0 | 63.6% | 1.54 kW | 55.5/51.2 kW | 13.6/14.1 m | 36.3/38.9 °C | 8/7 kPa | 2386/2201 l/h | 31.7/27.4 kW | 17.0/18.1 m | 28.5/31.1 °C | 3/2 kPa | 1364/1179 l/h | 37.1/34.6 kW | 46.4/43.9 kW | 37.1/56.7 kW | 62.4/87.4 kW | 11.8/12.6 °C | 12.7/13.5 °C | 13/30 kPa | 36/70 kPa | 5307/8118 l/h | 8941/12513 l/h | 0.0/32.5 kg/h | 23.5/63.9 kg/h | 37.1/29.7 kW | 41.6/39.1 kW | 37.1/45.1 kW | 50.9/75.8 kW | 11.8/14.2 °C | 14.3/15.1 °C | 13/19 kPa | 24/53 kPa | 5307/6459 l/h | 7282/10854 l/h | 0.0/22.6 kg/h | 13.6/54.0 kg/h | 60 dB(A) | 82 dB(A) | 47 dB | 66 dB | 69 dB | 74 dB | 77 dB | 76 dB | 74 dB | 67 dB | 7.4 l | 19.2 l | 329 kg
MHC-9-BD | 50°C | 60°C | 90°C | 800 kPa | 5000 m3/h | 150 kg/h | 3x400 V AC | +/-5% | 50 Hz | 3.6 kW | 5.9A | 13A | IP 54 | 9000.0 | 946.0 | 63.6% | 1.79 kW | 71.9/73.3 kW | 12.8/12.9 m | 41.2/40.7 °C | 12/13 kPa | 3090/3149 l/h | 41.3/42.7 kW | 16.7/17.0 m | 31.1/30.6 °C | 4/4 kPa | 1775/1834 l/h | 38.1/37.7 kW | 47.4/47.1 kW | 38.1/37.8 kW | 64.8/68.3 kW | 11.8/12.0 °C | 12.7/12.9 °C | 13/13 kPa | 39/43 kPa | 5451/5409 l/h | 9285/9785 l/h | 0.0/0.0 kg/h | 15.7/21.3 kg/h | 33.2/32.9 kW | 42.6/42.2 kW | 33.2/32.9 kW | 53.3/56.7 kW | 13.4/13.6 °C | 14.3/14.5 °C | 10/10 kPa | 26/30 kPa | 4756/4706 l/h | 7626/8126 l/h | 0.0/0.0 kg/h | 15.7/21.3 kg/h | 60 dB(A) | 82 dB(A) | 47 dB | 67 dB | 70 dB | 74 dB | 78 dB | 76 dB | 74 dB | 67 dB | 1242.0 | 1100.0 | 882.0 | 951.0 | 873.0 | 935.0 | 50.80 | 1622.0 | 846.0 | 38.10 | 500.0 | 1050.0 | 2496.0 | 1104.0 | 1220.0 | 1244.0 | 1149.0 | 25.40 | 7.4 l | 19.2 l | 388 kg | 50°C | 60°C | 90°C | 800 kPa | 5000 m3/h | 150 kg/h | 3x400 V AC | +/-5% | 50 Hz | 3.6 kW | 5.9A | 13A | IP 54 | 9000.0 | 946.0 | 63.6% | 1.56 kW | 71.2/65.7 kW | 12.2/12.7 m | 41.5/43.7 °C | 12/10 kPa | 3060/2823 l/h | 40.6/35.1 kW | 15.4/16.5 m | 31.4/33.6 °C | 4/3 kPa | 1746/1509 l/h | 37.1/34.6 kW | 46.4/43.9 kW | 37.1/56.7 kW | 62.4/87.4 kW | 11.8/12.6 °C | 12.7/13.5 °C | 13/30 kPa | 36/70 kPa | 5307/8118 l/h | 8941/12513 l/h | 0.0/32.5 kg/h | 23.5/63.9 kg/h | 37.1/29.7 kW | 41.6/39.1 kW | 37.1/45.1 kW | 50.9/75.8 kW | 11.8/14.2 °C | 14.3/15.1 °C | 13/19 kPa | 24/53 kPa | 5307/6459 l/h | 7282/10854 l/h | 0.0/22.6 kg/h | 13.6/54.0 kg/h | 60 dB(A) | 82 dB(A) | 47 dB | 66 dB | 69 dB | 74 dB | 77 dB | 76 dB | 74 dB | 67 dB | 7.4 l | 19.2 l | 329 kg
MHC-9-CD | 50°C | 60°C | 90°C | 800 kPa | 5000 m3/h | 150 kg/h | 3x400 V AC | +/-5% | 50 Hz | 3.6 kW | 5.9A | 13A | IP 54 | 9000.0 | 946.0 | 63.6% | 1.92 kW | 119.0/121.2 kW | 10.1/10.1 m | 56.8/56.5 °C | 18/19 kPa | 5113/5208 l/h | 71.0/73.2 kW | 12.9/12.9 m | 40.9/40.7 °C | 7/7 kPa | 3050/3145 l/h | 38.1/37.7 kW | 47.4/47.1 kW | 38.1/37.8 kW | 64.8/68.3 kW | 11.8/12.0 °C | 12.7/12.9 °C | 13/13 kPa | 39/43 kPa | 5451/5409 l/h | 9285/9785 l/h | 0.0/0.0 kg/h | 15.7/21.3 kg/h | 33.2/32.9 kW | 42.6/42.2 kW | 33.2/32.9 kW | 53.3/56.7 kW | 13.4/13.6 °C | 14.3/14.5 °C | 10/10 kPa | 26/30 kPa | 4756/4706 l/h | 7626/8126 l/h | 0.0/0.0 kg/h | 15.7/21.3 kg/h | 60 dB(A) | 82 dB(A) | 47 dB | 67 dB | 70 dB | 74 dB | 78 dB | 76 dB | 74 dB | 67 dB | 1242.0 | 1100.0 | 882.0 | 951.0 | 873.0 | 935.0 | 50.80 | 1622.0 | 846.0 | 38.10 | 500.0 | 1050.0 | 2496.0 | 1104.0 | 1220.0 | 1244.0 | 1149.0 | 25.40 | 12.4 l | 19.2 l | 399 kg | 50°C | 60°C | 90°C | 800 kPa | 5000 m3/h | 150 kg/h | 3x400 V AC | +/-5% | 50 Hz | 3.6 kW | 5.9A | 13A | IP 54 | 9000.0 | 946.0 | 63.6% | 1.68 kW | 117.9/109.1 kW | 9.8/10.2 m | 56.9/58.0 °C | 18/15 kPa | 5066/4686 l/h | 69.9/61.0 kW | 12.3/13.1 m | 41.1/42.1 °C | 6/5 kPa | 3003/2622 l/h | 37.1/34.6 kW | 46.4/43.9 kW | 37.1/56.7 kW | 62.4/87.4 kW | 11.8/12.6 °C | 12.7/13.5 °C | 13/30 kPa | 36/70 kPa | 5307/8118 l/h | 8941/12513 l/h | 0.0/32.5 kg/h | 23.5/63.9 kg/h | 37.1/29.7 kW | 41.6/39.1 kW | 37.1/45.1 kW | 50.9/75.8 kW | 11.8/14.2 °C | 14.3/15.1 °C | 13/19 kPa | 24/53 kPa | 5307/6459 l/h | 7282/10854 l/h | 0.0/22.6 kg/h | 13.6/54.0 kg/h | 60 dB(A) | 82 dB(A) | 47 dB | 66 dB | 69 dB | 74 dB | 77 dB | 76 dB | 74 dB | 67 dB | 12.4 l | 19.2 l | 340 kg