## List1
| TC-6-C | TC-9-C | TC-9-D
Extract air temperature max.##OTHER## | 50°C | 50°C | 50°C
Supply air temperature max.##OTHER## | 60°C | 60°C | 60°C
Temperature of the heating medium max.##OTHER## | 90°C | 90°C | 90°C
Pressure of the heating medium max.##OTHER## | 800 kPa | 800 kPa | 800 kPa
Air flow rate##OTHER## | 3100 m3/h | 5000 m3/h | 5000 m3/h
Condensate quantity##OTHER## | 90 kg/h | 150 kg/h | 150 kg/h
Supply voltage##OTHER## | 3x400 V AC | 3x400 V AC | 3x400 V AC
Permitted voltage tolerance##OTHER## | +/-5% | +/-5% | +/-5%
Frequency##OTHER## | 50 Hz | 50 Hz | 50 Hz
Connected load##OTHER## | 3.6 kW | 3.6 kW | 3.6 kW
Current consumption max.##OTHER## | 5.9A | 5.9A | 5.9A
Series fuse##OTHER## | 13A | 13A | 13A
Protection rating##OTHER## | IP 54 | IP 54 | IP 54
Nominal air flow rate##HVAC_AIR_FLOW##CUBIC_METERS_PER_HOUR | 6000.0 | 9000.0 | 9000.0
Floor area covered##AREA##SQUARE_METERS | 537.0 | 946.0 | 946.0
Static efficiency of the fans##OTHER## | 63.6% | 63.3% | 63.3%
Effective electric power input##OTHER## | 0.67 kW | 1.23 kW | 1.34 kW
Heat output 16/20 °C (80/60 °C)##OTHER## | 76.0/70.3 kW | 117.9/109.1 kW | 140.7/130.4 kW
Maximum mounting height 16/20 °C (80/60 °C)##OTHER## | 9.4/9.8 m | 9.8/10.2 m | 9.1/9.5 m
Supply air temperature 16/20 °C (80/60 °C)##OTHER## | 55.6/56.8 °C | 56.9/58.0 °C | 64.4/65.0 °C
Water pressure drop 16/20 °C (80/60 °C)##OTHER## | 18/16 kPa | 18/15 kPa | 15/13 kPa
Water quantity 16/20 °C (80/60 °C)##OTHER## | 3267/3022 l/h | 5066/4686 l/h | 6045/5600 l/h
Heat output 16/20 °C (60/40 °C)##OTHER## | 45.0/39.3 kW | 69.9/61.0 kW | 85.4/75.1 kW
Maximum mounting height 16/20 °C (60/40 °C)##OTHER## | 11.8/12.5 m | 12.3/13.1 m | 11.3/12.0 m
Supply air temperature 16/20 °C (60/40 °C)##OTHER## | 40.3/41.5 °C | 41.1/42.1 °C | 46.2/46.8 °C
Water pressure drop 16/20 °C (60/40 °C)##OTHER## | 6/5 kPa | 6/5 kPa | 5/4 kPa
Water quantity 16/20 °C (60/40 °C)##OTHER## | 1935/1690 l/h | 3003/2622 l/h | 3670/3225 l/h
Sensible cooling capacity 22 °C (50/70 %) - 6/12 °C##OTHER## | 20.4/18.5 kW | 31.4/28.4 kW | 37.1/34.6 kW
Sensible cooling capacity 26 °C (50/70 %) - 6/12 °C##OTHER## | 25.2/23.2 kW | 38.8/35.9 kW | 46.4/43.9 kW
Total cooling capacity 22 °C (50/70 %) - 6/12 °C##OTHER## | 20.4/27.7 kW | 31.4/44.7 kW | 37.1/56.7 kW
Total cooling capacity 26 °C (50/70 %) - 6/12 °C##OTHER## | 31.1/43.7 kW | 49.9/69.8 kW | 62.4/87.4 kW
Supply air temperature 22 °C (50/70 %) - 6/12 °C##OTHER## | 13.9/14.9 °C | 13.6/14.6 °C | 11.8/12.6 °C
Supply air temperature 26 °C (50/70 %) - 6/12 °C##OTHER## | 15.5/16.5 °C | 15.2/16.2 °C | 12.7/13.5 °C
Water pressure drop 22 °C (50/70 %) - 6/12 °C##OTHER## | 15/28 kPa | 15/31 kPa | 13/30 kPa
Water pressure drop 26 °C (50/70 %) - 6/12 °C##OTHER## | 36/71 kPa | 38/75 kPa | 36/70 kPa
Water quantity 22 °C (50/70 %) - 6/12 °C##OTHER## | 2925/3960 l/h | 4496/6401 l/h | 5307/8118 l/h
Water quantity 26 °C (50/70 %) - 6/12 °C##OTHER## | 4448/6263 l/h | 7149/9989 l/h | 8941/12513 l/h
Condensate quantity 22 °C (50/70 %) - 6/12 °C##OTHER## | 0.0/13.5 kg/h | 0.0/23.9 kg/h | 0.0/32.5 kg/h
Condensate quantity 26 °C (50/70 %) - 6/12 °C##OTHER## | 8.6/30.2 kg/h | 16.3/49.8 kg/h | 23.5/63.9 kg/h
Sensible cooling capacity 22 °C (50/70 %) - 8/14 °C##OTHER## | 18.0/16.0 kW | 27.6/24.6 kW | 32.2/29.7 kW
Sensible cooling capacity 26 °C (50/70 %) - 8/14 °C##OTHER## | 22.7/20.8 kW | 35.0/32.0 kW | 41.6/39.1 kW
Total cooling capacity 22 °C (50/70 %) - 8/14 °C##OTHER## | 18.0/21.4 kW | 27.6/28.2 kW | 32.2/45.1 kW
Total cooling capacity 26 °C (50/70 %) - 8/14 °C##OTHER## | 24.8/37.5 kW | 35.0/53.2 kW | 50.9/75.8 kW
Supply air temperature 22 °C (50/70 %) - 8/14 °C##OTHER## | 15.1/16.1 °C | 14.9/15.9 °C | 13.4/14.2 °C
Supply air temperature 26 °C (50/70 %) - 8/14 °C##OTHER## | 16.7/17.7 °C | 16.4/17.4 °C | 14.3/15.1 °C
Water pressure drop 22 °C (50/70 %) - 8/14 °C##OTHER## | 12/17 kPa | 12/12 kPa | 10/19 kPa
Water pressure drop 26 °C (50/70 %) - 8/14 °C##OTHER## | 23/52 kPa | 19/44 kPa | 24/53 kPa
Water quantity 22 °C (50/70 %) - 8/14 °C##OTHER## | 2573/3064 l/h | 3947/4031 l/h | 4613/6459 l/h
Water quantity 26 °C (50/70 %) - 8/14 °C##OTHER## | 3552/5367 l/h | 5013/7619 l/h | 7282/10854 l/h
Condensate quantity 22 °C (50/70 %) - 8/14 °C##OTHER## | 0.0/7.9 kg/h | 0.0/5.2 kg/h | 0.0/22.6 kg/h
Condensate quantity 26 °C (50/70 %) - 8/14 °C##OTHER## | 3.0/24.6 kg/h | 0.0/31.1 kg/h | 13.6/54.0 kg/h
Sound pressure level (at a distance of 5 m)##OTHER## | 51 dB(A) | 59 dB(A) | 59 dB(A)
Total sound power level##OTHER## | 73 dB(A) | 81 dB(A) | 81 dB(A)
Octave sound power level - 63 Hz##OTHER## | 41 dB | 49 dB | 49 dB
Octave sound power level - 125 Hz##OTHER## | 59 dB | 67 dB | 67 dB
Octave sound power level - 250 Hz##OTHER## | 62 dB | 70 dB | 70 dB
Octave sound power level - 500 Hz##OTHER## | 65 dB | 73 dB | 73 dB
Octave sound power level - 1000 Hz##OTHER## | 67 dB | 75 dB | 75 dB
Octave sound power level - 2000 Hz##OTHER## | 67 dB | 75 dB | 75 dB
Octave sound power level - 4000 Hz##OTHER## | 66 dB | 74 dB | 74 dB
Octave sound power level - 8000 Hz##OTHER## | 61 dB | 68 dB | 68 dB
(X)##LENGTH##MILLIMETERS | 850.0 | 930.0 | 930.0
A##LENGTH##MILLIMETERS | 900.0 | 1100.0 | 1100.0
B##LENGTH##MILLIMETERS | 1344.0 | 1430.0 | 1430.0
E##LENGTH##MILLIMETERS | 594.0 | 846.0 | 846.0
F##LENGTH##MILLIMETERS | 758.0 | 882.0 | 882.0
G##LENGTH##MILLIMETERS | 77.0 | 93.0 | 85.0
H##LENGTH##MILLIMETERS | 155.0 | 171.0 | 180.0
I##LENGTH##MILLIMETERS | 760.0 | 935.0 | 935.0
K##LENGTH##MILLIMETERS | 521.0 | 558.0 | 558.0
N##LENGTH##MILLIMETERS | 1030.0 | 1230.0 | 1230.0
R##LENGTH##MILLIMETERS | 1375.0 | 1463.0 | 1463.0
J##LENGTH##MILLIMETERS | 31.75 | 38.10 | 50.80
M##LENGTH##MILLIMETERS | 25.40 | 25.40 | 25.40
Water content of heating/cooling coil##OTHER## | 7.9 l | 12.4 l | 19.2 l
Weight##OTHER## | 216 kg | 265 kg | 276 kg
COBIE Extract air temperature max.##OTHER## | 50°C | 50°C | 50°C
COBIE Supply air temperature max.##OTHER## | 60°C | 60°C | 60°C
COBIE Temperature of the heating medium max.##OTHER## | 90°C | 90°C | 90°C
COBIE Pressure of the heating medium max.##OTHER## | 800 kPa | 800 kPa | 800 kPa
COBIE Air flow rate##OTHER## | 3100 m3/h | 5000 m3/h | 5000 m3/h
COBIE Condensate quantity##OTHER## | 90 kg/h | 150 kg/h | 150 kg/h
COBIE Supply voltage##OTHER## | 3x400 V AC | 3x400 V AC | 3x400 V AC
COBIE Permitted voltage tolerance##OTHER## | +/-5% | +/-5% | +/-5%
COBIE Frequency##OTHER## | 50 Hz | 50 Hz | 50 Hz
COBIE Connected load##OTHER## | 1.5 kW | 1.5 kW | 1.5 kW
COBIE Current consumption max.##OTHER## | 2.9A | 2.9A | 2.9A
COBIE Series fuse##OTHER## | 13A | 13A | 13A
COBIE Protection rating##OTHER## | IP 54 | IP 54 | IP 54
COBIE Nominal air flow rate##OTHER## | 6000.0 | 6000.0 | 6000.0
COBIE Floor area covered##OTHER## | 537.0 | 537.0 | 537.0
COBIE Static efficiency of the fans##OTHER## | 48.5% | 48.5% | 48.5%
COBIE Effective electric power input##OTHER## | 0.46 kW | 0.53 kW | 0.74 kW
COBIE Heat output 16/20 °C (80/60 °C)##OTHER## | 32.8/30.3 kW | 47.0/43.4 kW | 76.0/70.3 kW
COBIE Maximum mounting height 16/20 °C (80/60 °C)##OTHER## | 13.4/14.0 m | 11.6/12.0 m | 9.4/9.8 m
COBIE Supply air temperature 16/20 °C (80/60 °C)##OTHER## | 34.2/37.0 °C | 41.3/43.5 °C | 55.6/56.8 °C
COBIE Water pressure drop 16/20 °C (80/60 °C)##OTHER## | 7/6 kPa | 13/11 kPa | 18/16 kPa
COBIE Water quantity 16/20 °C (80/60 °C)##OTHER## | 1410/1301 l/h | 2020/1864 l/h | 3267/3022 l/h
COBIE Heat output 16/20 °C (60/40 °C)##OTHER## | 18.8/16.2 kW | 26.9/23.3 kW | 45.0/39.3 kW
COBIE Maximum mounting height 16/20 °C (60/40 °C)##OTHER## | 16.8/17.9 m | 14.6/15.5 m | 11.8/12.5 m
COBIE Supply air temperature 16/20 °C (60/40 °C)##OTHER## | 27.3/30.0 °C | 31.1/33.5 °C | 40.3/41.5 °C
COBIE Water pressure drop 16/20 °C (60/40 °C)##OTHER## | 2/2 kPa | 4/3 kPa | 6/5 kPa
COBIE Water quantity 16/20 °C (60/40 °C)##OTHER## | 807/697 l/h | 1157/1001 l/h | 1935/1690 l/h
COBIE Sensible cooling capacity 22 °C (50/70 %) - 6/12 °C##OTHER## | 20.4/18.5 kW | 31.4/28.4 kW | 37.1/34.6 kW
COBIE Sensible cooling capacity 26 °C (50/70 %) - 6/12 °C##OTHER## | 25.2/23.2 kW | 38.8/35.9 kW | 46.4/43.9 kW
COBIE Total cooling capacity 22 °C (50/70 %) - 6/12 °C##OTHER## | 20.4/27.7 kW | 31.4/44.7 kW | 37.1/56.7 kW
COBIE Total cooling capacity 26 °C (50/70 %) - 6/12 °C##OTHER## | 31.1/43.7 kW | 49.9/69.8 kW | 62.4/87.4 kW
COBIE Supply air temperature 22 °C (50/70 %) - 6/12 °C##OTHER## | 13.9/14.9 °C | 13.6/14.6 °C | 11.8/12.6 °C
COBIE Supply air temperature 26 °C (50/70 %) - 6/12 °C##OTHER## | 15.5/16.5 °C | 15.2/16.2 °C | 12.7/13.5 °C
COBIE Water pressure drop 22 °C (50/70 %) - 6/12 °C##OTHER## | 15/28 kPa | 15/31 kPa | 13/30 kPa
COBIE Water pressure drop 26 °C (50/70 %) - 6/12 °C##OTHER## | 36/71 kPa | 38/75 kPa | 36/70 kPa
COBIE Water quantity 22 °C (50/70 %) - 6/12 °C##OTHER## | 2925/3960 l/h | 4496/6401 l/h | 5307/8118 l/h
COBIE Water quantity 26 °C (50/70 %) - 6/12 °C##OTHER## | 4448/6263 l/h | 7149/9989 l/h | 8941/12513 l/h
COBIE Condensate quantity 22 °C (50/70 %) - 6/12 °C##OTHER## | 0.0/13.5 kg/h | 0.0/23.9 kg/h | 0.0/32.5 kg/h
COBIE Condensate quantity 26 °C (50/70 %) - 6/12 °C##OTHER## | 8.6/30.2 kg/h | 16.3/49.8 kg/h | 23.5/63.9 kg/h
COBIE Sensible cooling capacity 22 °C (50/70 %) - 8/14 °C##OTHER## | 18.0/16.0 kW | 27.6/24.6 kW | 32.2/29.7 kW
COBIE Sensible cooling capacity 26 °C (50/70 %) - 8/14 °C##OTHER## | 22.7/20.8 kW | 35.0/32.0 kW | 41.6/39.1 kW
COBIE Total cooling capacity 22 °C (50/70 %) - 8/14 °C##OTHER## | 18.0/21.4 kW | 27.6/28.2 kW | 32.2/45.1 kW
COBIE Total cooling capacity 26 °C (50/70 %) - 8/14 °C##OTHER## | 24.8/37.5 kW | 35.0/53.2 kW | 50.9/75.8 kW
COBIE Supply air temperature 22 °C (50/70 %) - 8/14 °C##OTHER## | 15.1/16.1 °C | 14.9/15.9 °C | 13.4/14.2 °C
COBIE Supply air temperature 26 °C (50/70 %) - 8/14 °C##OTHER## | 16.7/17.7 °C | 16.4/17.4 °C | 14.3/15.1 °C
COBIE Water pressure drop 22 °C (50/70 %) - 8/14 °C##OTHER## | 12/17 kPa | 12/12 kPa | 10/19 kPa
COBIE Water pressure drop 26 °C (50/70 %) - 8/14 °C##OTHER## | 23/52 kPa | 19/44 kPa | 24/53 kPa
COBIE Water quantity 22 °C (50/70 %) - 8/14 °C##OTHER## | 2573/3064 l/h | 3947/4031 l/h | 4613/6459 l/h
COBIE Water quantity 26 °C (50/70 %) - 8/14 °C##OTHER## | 3552/5367 l/h | 5013/7619 l/h | 7282/10854 l/h
COBIE Condensate quantity 22 °C (50/70 %) - 8/14 °C##OTHER## | 0.0/7.9 kg/h | 0.0/5.2 kg/h | 0.0/22.6 kg/h
COBIE Condensate quantity 26 °C (50/70 %) - 8/14 °C##OTHER## | 3.0/24.6 kg/h | 0.0/31.1 kg/h | 13.6/54.0 kg/h
COBIE Sound pressure level (at a distance of 5 m)##OTHER## | 55 dB(A) | 55 dB(A) | 55 dB(A)
COBIE Total sound power level##OTHER## | 77 dB(A) | 77 dB(A) | 77 dB(A)
COBIE Octave sound power level - 63 Hz##OTHER## | 55 dB | 55 dB | 55 dB
COBIE Octave sound power level - 125 Hz##OTHER## | 60 dB | 60 dB | 60 dB
COBIE Octave sound power level - 250 Hz##OTHER## | 65 dB | 65 dB | 65 dB
COBIE Octave sound power level - 500 Hz##OTHER## | 70 dB | 70 dB | 70 dB
COBIE Octave sound power level - 1000 Hz##OTHER## | 74 dB | 74 dB | 74 dB
COBIE Octave sound power level - 2000 Hz##OTHER## | 70 dB | 70 dB | 70 dB
COBIE Octave sound power level - 4000 Hz##OTHER## | 64 dB | 64 dB | 64 dB
COBIE Octave sound power level - 8000 Hz##OTHER## | 56 dB | 56 dB | 56 dB
COBIE Water content of heating/cooling coil##OTHER## | 4.6 l | 4.6 l | 7.9 l
COBIE Weight##OTHER## | 104 kg | 104 kg | 111 kg