## List1
| Extract air temperature max.##OTHER## | Supply air temperature max.##OTHER## | Temperature of the heating medium max.##OTHER## | Pressure of the heating medium max.##OTHER## | Air flow rate##OTHER## | Condensate quantity##OTHER## | Supply voltage##OTHER## | Permitted voltage tolerance##OTHER## | Frequency##OTHER## | Connected load##OTHER## | Current consumption max.##OTHER## | Series fuse##OTHER## | Protection rating##OTHER## | Nominal air flow rate##HVAC_AIR_FLOW##CUBIC_METERS_PER_HOUR | Floor area covered##AREA##SQUARE_METERS | Static efficiency of the fans##OTHER## | Effective electric power input##OTHER## | Heat output 16/20 °C (80/60 °C)##OTHER## | Maximum mounting height 16/20 °C (80/60 °C)##OTHER## | Supply air temperature 16/20 °C (80/60 °C)##OTHER## | Water pressure drop 16/20 °C (80/60 °C)##OTHER## | Water quantity 16/20 °C (80/60 °C)##OTHER## | Heat output 16/20 °C (60/40 °C)##OTHER## | Maximum mounting height 16/20 °C (60/40 °C)##OTHER## | Supply air temperature 16/20 °C (60/40 °C)##OTHER## | Water pressure drop 16/20 °C (60/40 °C)##OTHER## | Water quantity 16/20 °C (60/40 °C)##OTHER## | Sensible cooling capacity 22 °C (50/70 %) - 6/12 °C##OTHER## | Sensible cooling capacity 26 °C (50/70 %) - 6/12 °C##OTHER## | Total cooling capacity 22 °C (50/70 %) - 6/12 °C##OTHER## | Total cooling capacity 26 °C (50/70 %) - 6/12 °C##OTHER## | Supply air temperature 22 °C (50/70 %) - 6/12 °C##OTHER## | Supply air temperature 26 °C (50/70 %) - 6/12 °C##OTHER## | Water pressure drop 22 °C (50/70 %) - 6/12 °C##OTHER## | Water pressure drop 26 °C (50/70 %) - 6/12 °C##OTHER## | Water quantity 22 °C (50/70 %) - 6/12 °C##OTHER## | Water quantity 26 °C (50/70 %) - 6/12 °C##OTHER## | Condensate quantity 22 °C (50/70 %) - 6/12 °C##OTHER## | Condensate quantity 26 °C (50/70 %) - 6/12 °C##OTHER## | Sensible cooling capacity 22 °C (50/70 %) - 8/14 °C##OTHER## | Sensible cooling capacity 26 °C (50/70 %) - 8/14 °C##OTHER## | Total cooling capacity 22 °C (50/70 %) - 8/14 °C##OTHER## | Total cooling capacity 26 °C (50/70 %) - 8/14 °C##OTHER## | Supply air temperature 22 °C (50/70 %) - 8/14 °C##OTHER## | Supply air temperature 26 °C (50/70 %) - 8/14 °C##OTHER## | Water pressure drop 22 °C (50/70 %) - 8/14 °C##OTHER## | Water pressure drop 26 °C (50/70 %) - 8/14 °C##OTHER## | Water quantity 22 °C (50/70 %) - 8/14 °C##OTHER## | Water quantity 26 °C (50/70 %) - 8/14 °C##OTHER## | Condensate quantity 22 °C (50/70 %) - 8/14 °C##OTHER## | Condensate quantity 26 °C (50/70 %) - 8/14 °C##OTHER## | Sound pressure level (at a distance of 5 m)##OTHER## | Total sound power level##OTHER## | Octave sound power level - 63 Hz##OTHER## | Octave sound power level - 125 Hz##OTHER## | Octave sound power level - 250 Hz##OTHER## | Octave sound power level - 500 Hz##OTHER## | Octave sound power level - 1000 Hz##OTHER## | Octave sound power level - 2000 Hz##OTHER## | Octave sound power level - 4000 Hz##OTHER## | Octave sound power level - 8000 Hz##OTHER## | (X)##LENGTH##MILLIMETERS | A##LENGTH##MILLIMETERS | B##LENGTH##MILLIMETERS | E##LENGTH##MILLIMETERS | F##LENGTH##MILLIMETERS | G##LENGTH##MILLIMETERS | H##LENGTH##MILLIMETERS | I##LENGTH##MILLIMETERS | K##LENGTH##MILLIMETERS | N##LENGTH##MILLIMETERS | R##LENGTH##MILLIMETERS | J##LENGTH##MILLIMETERS | M##LENGTH##MILLIMETERS | Water content of heating/cooling coil##OTHER## | Weight##OTHER## | COBIE Extract air temperature max.##OTHER## | COBIE Supply air temperature max.##OTHER## | COBIE Temperature of the heating medium max.##OTHER## | COBIE Pressure of the heating medium max.##OTHER## | COBIE Air flow rate##OTHER## | COBIE Condensate quantity##OTHER## | COBIE Supply voltage##OTHER## | COBIE Permitted voltage tolerance##OTHER## | COBIE Frequency##OTHER## | COBIE Connected load##OTHER## | COBIE Current consumption max.##OTHER## | COBIE Series fuse##OTHER## | COBIE Protection rating##OTHER## | COBIE Nominal air flow rate##OTHER## | COBIE Floor area covered##OTHER## | COBIE Static efficiency of the fans##OTHER## | COBIE Effective electric power input##OTHER## | COBIE Heat output 16/20 °C (80/60 °C)##OTHER## | COBIE Maximum mounting height 16/20 °C (80/60 °C)##OTHER## | COBIE Supply air temperature 16/20 °C (80/60 °C)##OTHER## | COBIE Water pressure drop 16/20 °C (80/60 °C)##OTHER## | COBIE Water quantity 16/20 °C (80/60 °C)##OTHER## | COBIE Heat output 16/20 °C (60/40 °C)##OTHER## | COBIE Maximum mounting height 16/20 °C (60/40 °C)##OTHER## | COBIE Supply air temperature 16/20 °C (60/40 °C)##OTHER## | COBIE Water pressure drop 16/20 °C (60/40 °C)##OTHER## | COBIE Water quantity 16/20 °C (60/40 °C)##OTHER## | COBIE Sensible cooling capacity 22 °C (50/70 %) - 6/12 °C##OTHER## | COBIE Sensible cooling capacity 26 °C (50/70 %) - 6/12 °C##OTHER## | COBIE Total cooling capacity 22 °C (50/70 %) - 6/12 °C##OTHER## | COBIE Total cooling capacity 26 °C (50/70 %) - 6/12 °C##OTHER## | COBIE Supply air temperature 22 °C (50/70 %) - 6/12 °C##OTHER## | COBIE Supply air temperature 26 °C (50/70 %) - 6/12 °C##OTHER## | COBIE Water pressure drop 22 °C (50/70 %) - 6/12 °C##OTHER## | COBIE Water pressure drop 26 °C (50/70 %) - 6/12 °C##OTHER## | COBIE Water quantity 22 °C (50/70 %) - 6/12 °C##OTHER## | COBIE Water quantity 26 °C (50/70 %) - 6/12 °C##OTHER## | COBIE Condensate quantity 22 °C (50/70 %) - 6/12 °C##OTHER## | COBIE Condensate quantity 26 °C (50/70 %) - 6/12 °C##OTHER## | COBIE Sensible cooling capacity 22 °C (50/70 %) - 8/14 °C##OTHER## | COBIE Sensible cooling capacity 26 °C (50/70 %) - 8/14 °C##OTHER## | COBIE Total cooling capacity 22 °C (50/70 %) - 8/14 °C##OTHER## | COBIE Total cooling capacity 26 °C (50/70 %) - 8/14 °C##OTHER## | COBIE Supply air temperature 22 °C (50/70 %) - 8/14 °C##OTHER## | COBIE Supply air temperature 26 °C (50/70 %) - 8/14 °C##OTHER## | COBIE Water pressure drop 22 °C (50/70 %) - 8/14 °C##OTHER## | COBIE Water pressure drop 26 °C (50/70 %) - 8/14 °C##OTHER## | COBIE Water quantity 22 °C (50/70 %) - 8/14 °C##OTHER## | COBIE Water quantity 26 °C (50/70 %) - 8/14 °C##OTHER## | COBIE Condensate quantity 22 °C (50/70 %) - 8/14 °C##OTHER## | COBIE Condensate quantity 26 °C (50/70 %) - 8/14 °C##OTHER## | COBIE Sound pressure level (at a distance of 5 m)##OTHER## | COBIE Total sound power level##OTHER## | COBIE Octave sound power level - 63 Hz##OTHER## | COBIE Octave sound power level - 125 Hz##OTHER## | COBIE Octave sound power level - 250 Hz##OTHER## | COBIE Octave sound power level - 500 Hz##OTHER## | COBIE Octave sound power level - 1000 Hz##OTHER## | COBIE Octave sound power level - 2000 Hz##OTHER## | COBIE Octave sound power level - 4000 Hz##OTHER## | COBIE Octave sound power level - 8000 Hz##OTHER## | COBIE Water content of heating/cooling coil##OTHER## | COBIE Weight##OTHER##
TC-6-C | 50°C | 60°C | 90°C | 800 kPa | 3100 m3/h | 90 kg/h | 3x400 V AC | +/-5% | 50 Hz | 3.6 kW | 5.9A | 13A | IP 54 | 6000.0 | 537.0 | 63.6% | 0.67 kW | 76.0/70.3 kW | 9.4/9.8 m | 55.6/56.8 °C | 18/16 kPa | 3267/3022 l/h | 45.0/39.3 kW | 11.8/12.5 m | 40.3/41.5 °C | 6/5 kPa | 1935/1690 l/h | 20.4/18.5 kW | 25.2/23.2 kW | 20.4/27.7 kW | 31.1/43.7 kW | 13.9/14.9 °C | 15.5/16.5 °C | 15/28 kPa | 36/71 kPa | 2925/3960 l/h | 4448/6263 l/h | 0.0/13.5 kg/h | 8.6/30.2 kg/h | 18.0/16.0 kW | 22.7/20.8 kW | 18.0/21.4 kW | 24.8/37.5 kW | 15.1/16.1 °C | 16.7/17.7 °C | 12/17 kPa | 23/52 kPa | 2573/3064 l/h | 3552/5367 l/h | 0.0/7.9 kg/h | 3.0/24.6 kg/h | 51 dB(A) | 73 dB(A) | 41 dB | 59 dB | 62 dB | 65 dB | 67 dB | 67 dB | 66 dB | 61 dB | 850.0 | 900.0 | 1344.0 | 594.0 | 758.0 | 77.0 | 155.0 | 760.0 | 521.0 | 1030.0 | 1375.0 | 31.75 | 25.40 | 7.9 l | 216 kg | 50°C | 60°C | 90°C | 800 kPa | 3100 m3/h | 90 kg/h | 3x400 V AC | +/-5% | 50 Hz | 1.5 kW | 2.9A | 13A | IP 54 | 6000.0 | 537.0 | 48.5% | 0.46 kW | 32.8/30.3 kW | 13.4/14.0 m | 34.2/37.0 °C | 7/6 kPa | 1410/1301 l/h | 18.8/16.2 kW | 16.8/17.9 m | 27.3/30.0 °C | 2/2 kPa | 807/697 l/h | 20.4/18.5 kW | 25.2/23.2 kW | 20.4/27.7 kW | 31.1/43.7 kW | 13.9/14.9 °C | 15.5/16.5 °C | 15/28 kPa | 36/71 kPa | 2925/3960 l/h | 4448/6263 l/h | 0.0/13.5 kg/h | 8.6/30.2 kg/h | 18.0/16.0 kW | 22.7/20.8 kW | 18.0/21.4 kW | 24.8/37.5 kW | 15.1/16.1 °C | 16.7/17.7 °C | 12/17 kPa | 23/52 kPa | 2573/3064 l/h | 3552/5367 l/h | 0.0/7.9 kg/h | 3.0/24.6 kg/h | 55 dB(A) | 77 dB(A) | 55 dB | 60 dB | 65 dB | 70 dB | 74 dB | 70 dB | 64 dB | 56 dB | 4.6 l | 104 kg
TC-9-C | 50°C | 60°C | 90°C | 800 kPa | 5000 m3/h | 150 kg/h | 3x400 V AC | +/-5% | 50 Hz | 3.6 kW | 5.9A | 13A | IP 54 | 9000.0 | 946.0 | 63.3% | 1.23 kW | 117.9/109.1 kW | 9.8/10.2 m | 56.9/58.0 °C | 18/15 kPa | 5066/4686 l/h | 69.9/61.0 kW | 12.3/13.1 m | 41.1/42.1 °C | 6/5 kPa | 3003/2622 l/h | 31.4/28.4 kW | 38.8/35.9 kW | 31.4/44.7 kW | 49.9/69.8 kW | 13.6/14.6 °C | 15.2/16.2 °C | 15/31 kPa | 38/75 kPa | 4496/6401 l/h | 7149/9989 l/h | 0.0/23.9 kg/h | 16.3/49.8 kg/h | 27.6/24.6 kW | 35.0/32.0 kW | 27.6/28.2 kW | 35.0/53.2 kW | 14.9/15.9 °C | 16.4/17.4 °C | 12/12 kPa | 19/44 kPa | 3947/4031 l/h | 5013/7619 l/h | 0.0/5.2 kg/h | 0.0/31.1 kg/h | 59 dB(A) | 81 dB(A) | 49 dB | 67 dB | 70 dB | 73 dB | 75 dB | 75 dB | 74 dB | 68 dB | 930.0 | 1100.0 | 1430.0 | 846.0 | 882.0 | 93.0 | 171.0 | 935.0 | 558.0 | 1230.0 | 1463.0 | 38.10 | 25.40 | 12.4 l | 265 kg | 50°C | 60°C | 90°C | 800 kPa | 5000 m3/h | 150 kg/h | 3x400 V AC | +/-5% | 50 Hz | 1.5 kW | 2.9A | 13A | IP 54 | 6000.0 | 537.0 | 48.5% | 0.53 kW | 47.0/43.4 kW | 11.6/12.0 m | 41.3/43.5 °C | 13/11 kPa | 2020/1864 l/h | 26.9/23.3 kW | 14.6/15.5 m | 31.1/33.5 °C | 4/3 kPa | 1157/1001 l/h | 31.4/28.4 kW | 38.8/35.9 kW | 31.4/44.7 kW | 49.9/69.8 kW | 13.6/14.6 °C | 15.2/16.2 °C | 15/31 kPa | 38/75 kPa | 4496/6401 l/h | 7149/9989 l/h | 0.0/23.9 kg/h | 16.3/49.8 kg/h | 27.6/24.6 kW | 35.0/32.0 kW | 27.6/28.2 kW | 35.0/53.2 kW | 14.9/15.9 °C | 16.4/17.4 °C | 12/12 kPa | 19/44 kPa | 3947/4031 l/h | 5013/7619 l/h | 0.0/5.2 kg/h | 0.0/31.1 kg/h | 55 dB(A) | 77 dB(A) | 55 dB | 60 dB | 65 dB | 70 dB | 74 dB | 70 dB | 64 dB | 56 dB | 4.6 l | 104 kg
TC-9-D | 50°C | 60°C | 90°C | 800 kPa | 5000 m3/h | 150 kg/h | 3x400 V AC | +/-5% | 50 Hz | 3.6 kW | 5.9A | 13A | IP 54 | 9000.0 | 946.0 | 63.3% | 1.34 kW | 140.7/130.4 kW | 9.1/9.5 m | 64.4/65.0 °C | 15/13 kPa | 6045/5600 l/h | 85.4/75.1 kW | 11.3/12.0 m | 46.2/46.8 °C | 5/4 kPa | 3670/3225 l/h | 37.1/34.6 kW | 46.4/43.9 kW | 37.1/56.7 kW | 62.4/87.4 kW | 11.8/12.6 °C | 12.7/13.5 °C | 13/30 kPa | 36/70 kPa | 5307/8118 l/h | 8941/12513 l/h | 0.0/32.5 kg/h | 23.5/63.9 kg/h | 32.2/29.7 kW | 41.6/39.1 kW | 32.2/45.1 kW | 50.9/75.8 kW | 13.4/14.2 °C | 14.3/15.1 °C | 10/19 kPa | 24/53 kPa | 4613/6459 l/h | 7282/10854 l/h | 0.0/22.6 kg/h | 13.6/54.0 kg/h | 59 dB(A) | 81 dB(A) | 49 dB | 67 dB | 70 dB | 73 dB | 75 dB | 75 dB | 74 dB | 68 dB | 930.0 | 1100.0 | 1430.0 | 846.0 | 882.0 | 85.0 | 180.0 | 935.0 | 558.0 | 1230.0 | 1463.0 | 50.80 | 25.40 | 19.2 l | 276 kg | 50°C | 60°C | 90°C | 800 kPa | 5000 m3/h | 150 kg/h | 3x400 V AC | +/-5% | 50 Hz | 1.5 kW | 2.9A | 13A | IP 54 | 6000.0 | 537.0 | 48.5% | 0.74 kW | 76.0/70.3 kW | 9.4/9.8 m | 55.6/56.8 °C | 18/16 kPa | 3267/3022 l/h | 45.0/39.3 kW | 11.8/12.5 m | 40.3/41.5 °C | 6/5 kPa | 1935/1690 l/h | 37.1/34.6 kW | 46.4/43.9 kW | 37.1/56.7 kW | 62.4/87.4 kW | 11.8/12.6 °C | 12.7/13.5 °C | 13/30 kPa | 36/70 kPa | 5307/8118 l/h | 8941/12513 l/h | 0.0/32.5 kg/h | 23.5/63.9 kg/h | 32.2/29.7 kW | 41.6/39.1 kW | 32.2/45.1 kW | 50.9/75.8 kW | 13.4/14.2 °C | 14.3/15.1 °C | 10/19 kPa | 24/53 kPa | 4613/6459 l/h | 7282/10854 l/h | 0.0/22.6 kg/h | 13.6/54.0 kg/h | 55 dB(A) | 77 dB(A) | 55 dB | 60 dB | 65 dB | 70 dB | 74 dB | 70 dB | 64 dB | 56 dB | 7.9 l | 111 kg