## List1
| Extract air temperature max.##OTHER## | Supply air temperature max.##OTHER## | Temperature of the heating medium max.##OTHER## | Pressure of the heating medium max.##OTHER## | Supply voltage##OTHER## | Permitted voltage tolerance##OTHER## | Frequency##OTHER## | Connected load##OTHER## | Current consumption max.##OTHER## | Series fuse##OTHER## | Protection rating##OTHER## | Nominal air flow rate##HVAC_AIR_FLOW##CUBIC_METERS_PER_HOUR | Floor area covered##AREA##SQUARE_METERS | Static efficiency of the fans##OTHER## | Effective electric power input##OTHER## | Heat output 16/20 °C (80/60 °C)##OTHER## | Maximum mounting height 16/20 °C (80/60 °C)##OTHER## | Supply air temperature 16/20 °C (80/60 °C)##OTHER## | Water pressure drop 16/20 °C (80/60 °C)##OTHER## | Water quantity 16/20 °C (80/60 °C)##OTHER## | Heat output 16/20 °C (60/40 °C)##OTHER## | Maximum mounting height 16/20 °C (60/40 °C)##OTHER## | Supply air temperature 16/20 °C (60/40 °C)##OTHER## | Water pressure drop 16/20 °C (60/40 °C)##OTHER## | Water quantity 16/20 °C (60/40 °C)##OTHER## | Sound pressure level (at a distance of 5 m)##OTHER## | Total sound power level##OTHER## | Octave sound power level - 63 Hz##OTHER## | Octave sound power level - 125 Hz##OTHER## | Octave sound power level - 250 Hz##OTHER## | Octave sound power level - 500 Hz##OTHER## | Octave sound power level - 1000 Hz##OTHER## | Octave sound power level - 2000 Hz##OTHER## | Octave sound power level - 4000 Hz##OTHER## | Octave sound power level - 8000 Hz##OTHER## | A##LENGTH##MILLIMETERS | B##LENGTH##MILLIMETERS | C##LENGTH##MILLIMETERS | E##LENGTH##MILLIMETERS | F##LENGTH##MILLIMETERS | G##LENGTH##MILLIMETERS | H##LENGTH##MILLIMETERS | I##LENGTH##MILLIMETERS | K##LENGTH##MILLIMETERS | R##LENGTH##MILLIMETERS | J##LENGTH##MILLIMETERS | Water content of heating coil##OTHER## | Weight##OTHER## | COBIE Extract air temperature max.##OTHER## | COBIE Supply air temperature max.##OTHER## | COBIE Temperature of the heating medium max.##OTHER## | COBIE Pressure of the heating medium max.##OTHER## | COBIE Supply voltage##OTHER## | COBIE Permitted voltage tolerance##OTHER## | COBIE Frequency##OTHER## | COBIE Connected load##OTHER## | COBIE Current consumption max.##OTHER## | COBIE Series fuse##OTHER## | COBIE Protection rating##OTHER## | COBIE Nominal air flow rate##OTHER## | COBIE Floor area covered##OTHER## | COBIE Static efficiency of the fans##OTHER## | COBIE Effective electric power input##OTHER## | COBIE Heat output 16/20 °C (80/60 °C)##OTHER## | COBIE Maximum mounting height 16/20 °C (80/60 °C)##OTHER## | COBIE Supply air temperature 16/20 °C (80/60 °C)##OTHER## | COBIE Water pressure drop 16/20 °C (80/60 °C)##OTHER## | COBIE Water quantity 16/20 °C (80/60 °C)##OTHER## | COBIE Heat output 16/20 °C (60/40 °C)##OTHER## | COBIE Maximum mounting height 16/20 °C (60/40 °C)##OTHER## | COBIE Supply air temperature 16/20 °C (60/40 °C)##OTHER## | COBIE Water pressure drop 16/20 °C (60/40 °C)##OTHER## | COBIE Water quantity 16/20 °C (60/40 °C)##OTHER## | COBIE Sound pressure level (at a distance of 5 m)##OTHER## | COBIE Total sound power level##OTHER## | COBIE Octave sound power level - 63 Hz##OTHER## | COBIE Octave sound power level - 125 Hz##OTHER## | COBIE Octave sound power level - 250 Hz##OTHER## | COBIE Octave sound power level - 500 Hz##OTHER## | COBIE Octave sound power level - 1000 Hz##OTHER## | COBIE Octave sound power level - 2000 Hz##OTHER## | COBIE Octave sound power level - 4000 Hz##OTHER## | COBIE Octave sound power level - 8000 Hz##OTHER## | COBIE Water content of heating coil##OTHER## | COBIE Weight##OTHER##
TH-6-A | 50°C | 60°C | 90°C | 800 kPa | 3x400 V AC | +/-5% | 50 Hz | 1.5 kW | 2.9A | 13A | IP 54 | 6000.0 | 537.0 | 48.5% | 0.46 kW | 32.8/30.3 kW | 13.4/14.0 m | 34.2/37.0 °C | 7/6 kPa | 1410/1301 l/h | 18.8/16.2 kW | 16.8/17.9 m | 27.3/30.0 °C | 2/2 kPa | 807/697 l/h | 55 dB(A) | 77 dB(A) | 55 dB | 60 dB | 65 dB | 70 dB | 74 dB | 70 dB | 64 dB | 56 dB | 900.0 | 905.0 | 415.0 | 594.0 | 758.0 | 322.0 | 244.0 | 760.0 | 1030.0 | 977.0 | 31.75 | 4.6 l | 104 kg | 50°C | 60°C | 90°C | 800 kPa | 3x400 V AC | +/-5% | 50 Hz | 1.5 kW | 2.9A | 13A | IP 54 | 6000.0 | 537.0 | 48.5% | 0.46 kW | 32.8/30.3 kW | 13.4/14.0 m | 34.2/37.0 °C | 7/6 kPa | 1410/1301 l/h | 18.8/16.2 kW | 16.8/17.9 m | 27.3/30.0 °C | 2/2 kPa | 807/697 l/h | 55 dB(A) | 77 dB(A) | 55 dB | 60 dB | 65 dB | 70 dB | 74 dB | 70 dB | 64 dB | 56 dB | 4.6 l | 104 kg
TH-6-B | 50°C | 60°C | 90°C | 800 kPa | 3x400 V AC | +/-5% | 50 Hz | 1.5 kW | 2.9A | 13A | IP 54 | 6000.0 | 537.0 | 48.5% | 0.53 kW | 47.0/43.4 kW | 11.6/12.0 m | 41.3/43.5 °C | 13/11 kPa | 2020/1864 l/h | 26.9/23.3 kW | 14.6/15.5 m | 31.1/33.5 °C | 4/3 kPa | 1157/1001 l/h | 55 dB(A) | 77 dB(A) | 55 dB | 60 dB | 65 dB | 70 dB | 74 dB | 70 dB | 64 dB | 56 dB | 900.0 | 905.0 | 415.0 | 594.0 | 758.0 | 322.0 | 244.0 | 760.0 | 1030.0 | 977.0 | 31.75 | 4.6 l | 104 kg | 50°C | 60°C | 90°C | 800 kPa | 3x400 V AC | +/-5% | 50 Hz | 1.5 kW | 2.9A | 13A | IP 54 | 6000.0 | 537.0 | 48.5% | 0.53 kW | 47.0/43.4 kW | 11.6/12.0 m | 41.3/43.5 °C | 13/11 kPa | 2020/1864 l/h | 26.9/23.3 kW | 14.6/15.5 m | 31.1/33.5 °C | 4/3 kPa | 1157/1001 l/h | 55 dB(A) | 77 dB(A) | 55 dB | 60 dB | 65 dB | 70 dB | 74 dB | 70 dB | 64 dB | 56 dB | 4.6 l | 104 kg
TH-6-C | 50°C | 60°C | 90°C | 800 kPa | 3x400 V AC | +/-5% | 50 Hz | 1.5 kW | 2.9A | 13A | IP 54 | 6000.0 | 537.0 | 48.5% | 0.74 kW | 76.0/70.3 kW | 9.4/9.8 m | 55.6/56.8 °C | 18/16 kPa | 3267/3022 l/h | 45.0/39.3 kW | 11.8/12.5 m | 40.3/41.5 °C | 6/5 kPa | 1935/1690 l/h | 55 dB(A) | 77 dB(A) | 55 dB | 60 dB | 65 dB | 70 dB | 74 dB | 70 dB | 64 dB | 56 dB | 900.0 | 905.0 | 415.0 | 594.0 | 758.0 | 322.0 | 244.0 | 760.0 | 1030.0 | 977.0 | 31.75 | 7.9 l | 111 kg | 50°C | 60°C | 90°C | 800 kPa | 3x400 V AC | +/-5% | 50 Hz | 1.5 kW | 2.9A | 13A | IP 54 | 6000.0 | 537.0 | 48.5% | 0.74 kW | 76.0/70.3 kW | 9.4/9.8 m | 55.6/56.8 °C | 18/16 kPa | 3267/3022 l/h | 45.0/39.3 kW | 11.8/12.5 m | 40.3/41.5 °C | 6/5 kPa | 1935/1690 l/h | 55 dB(A) | 77 dB(A) | 55 dB | 60 dB | 65 dB | 70 dB | 74 dB | 70 dB | 64 dB | 56 dB | 7.9 l | 111 kg
TH-9-A | 50°C | 60°C | 90°C | 800 kPa | 3x400 V AC | +/-5% | 50 Hz | 2.1 kW | 4.0A | 13A | IP 54 | 9000.0 | 946.0 | 43.0% | 0.84 kW | 55.5/51.2 kW | 13.6/14.1 m | 36.6/38.9 °C | 8/7 kPa | 2386/2201 l/h | 31.7/27.4 kW | 17.0/18.1 m | 28.5/31.1 °C | 3/2 kPa | 1364/1179 l/h | 58 dB(A) | 80 dB(A) | 61 dB | 65 dB | 69 dB | 73 dB | 75 dB | 75 dB | 70 dB | 63 dB | 1100.0 | 1050.0 | 480.0 | 846.0 | 882.0 | 367.0 | 289.0 | 935.0 | 1230.0 | 1152.0 | 38.10 | 7.4 l | 155 kg | 50°C | 60°C | 90°C | 800 kPa | 3x400 V AC | +/-5% | 50 Hz | 2.1 kW | 4.0A | 13A | IP 54 | 9000.0 | 946.0 | 43.0% | 0.84 kW | 55.5/51.2 kW | 13.6/14.1 m | 36.6/38.9 °C | 8/7 kPa | 2386/2201 l/h | 31.7/27.4 kW | 17.0/18.1 m | 28.5/31.1 °C | 3/2 kPa | 1364/1179 l/h | 58 dB(A) | 80 dB(A) | 61 dB | 65 dB | 69 dB | 73 dB | 75 dB | 75 dB | 70 dB | 63 dB | 7.4 l | 155 kg
TH-9-B | 50°C | 60°C | 90°C | 800 kPa | 3x400 V AC | +/-5% | 50 Hz | 2.1 kW | 4.0A | 13A | IP 54 | 9000.0 | 946.0 | 43.0% | 0.96 kW | 71.2/65.7 kW | 12.2/12.7 m | 41.5/43.7 °C | 12/10 kPa | 3060/2823 l/h | 40.6/35.1 kW | 15.4/16.5 m | 31.4/33.6 °C | 4/3 kPa | 1746/1509 l/h | 58 dB(A) | 80 dB(A) | 61 dB | 65 dB | 69 dB | 73 dB | 75 dB | 75 dB | 70 dB | 63 dB | 1100.0 | 1050.0 | 480.0 | 846.0 | 882.0 | 367.0 | 289.0 | 935.0 | 1230.0 | 1152.0 | 38.10 | 7.4 l | 155 kg | 50°C | 60°C | 90°C | 800 kPa | 3x400 V AC | +/-5% | 50 Hz | 2.1 kW | 4.0A | 13A | IP 54 | 9000.0 | 946.0 | 43.0% | 0.96 kW | 71.2/65.7 kW | 12.2/12.7 m | 41.5/43.7 °C | 12/10 kPa | 3060/2823 l/h | 40.6/35.1 kW | 15.4/16.5 m | 31.4/33.6 °C | 4/3 kPa | 1746/1509 l/h | 58 dB(A) | 80 dB(A) | 61 dB | 65 dB | 69 dB | 73 dB | 75 dB | 75 dB | 70 dB | 63 dB | 7.4 l | 155 kg
TH-9-C | 50°C | 60°C | 90°C | 800 kPa | 3x400 V AC | +/-5% | 50 Hz | 2.1 kW | 4.0A | 13A | IP 54 | 9000.0 | 946.0 | 43.0% | 1.26 kW | 117.9/109.1 kW | 9.8/10.2 m | 56.9/58.0 °C | 18/15 kPa | 5066/4686 l/h | 69.9/61.1 kW | 12.3/13.1 m | 41.1/42.1 °C | 6/5 kPa | 3003/2622 l/h | 58 dB(A) | 80 dB(A) | 61 dB | 65 dB | 69 dB | 73 dB | 75 dB | 75 dB | 70 dB | 63 dB | 1100.0 | 1050.0 | 480.0 | 846.0 | 882.0 | 367.0 | 289.0 | 935.0 | 1230.0 | 1152.0 | 38.10 | 12.4 l | 166 kg | 50°C | 60°C | 90°C | 800 kPa | 3x400 V AC | +/-5% | 50 Hz | 2.1 kW | 4.0A | 13A | IP 54 | 9000.0 | 946.0 | 43.0% | 1.26 kW | 117.9/109.1 kW | 9.8/10.2 m | 56.9/58.0 °C | 18/15 kPa | 5066/4686 l/h | 69.9/61.1 kW | 12.3/13.1 m | 41.1/42.1 °C | 6/5 kPa | 3003/2622 l/h | 58 dB(A) | 80 dB(A) | 61 dB | 65 dB | 69 dB | 73 dB | 75 dB | 75 dB | 70 dB | 63 dB | 12.4 l | 166 kg